## Inspection Register
Ex Inspection Register
| Project Name | : Explosion Proof (EX) Equipment - Inspection & Repair Works at DPE Onshore Facilities
| Client | : Dubai Petroleum Establishment
| Contractor | : Delta Solutions Engineering Services
| Date Updated | : 24 Sep 23 08:20 Hrs
Asset References |  |  | Location Details | [9 empty] | Equipment Tag Details | [6 empty] | Ex Protection Details | [10 empty] | Defect Analysis | [17 empty] | Corrective Actions
Sl. No. | RFID Reference | Inspection Reference | Location | Area | Sub-Area | GPS Co-ordinates | Zone | Gas Group | T-Class | IP Rating | Area Classification Drawing Number | Equipment Layout Drawing Number | Equipment Tag | Circuit ID | Description | Manufacturer | Type / Model | Serial Number | Equipment Category | ATEX Category | EPL | Protection Standard | Protection Type | Gas Group | T-Class | IP Rating | T-Ambient | Certification Body | Certification Number | Special Conditions | Equipment Type | Inspection Type | Inspection Checklist | Inspection Grade | Findings | Remedial Actions | Remarks if Any | Faulty Items | Inspection Photos | Inspection Status | Defect Category | Overall Condition | Isolations | Other Requirements | Material Requirements | Equipment Data Sheet | Inspected By | Inspected Date | Repairs Done | Existing Faults | Current Photos | Current Status | Defect Category | Current Condition | Isolations | Other Requirements | Repaired By | Repaired Date | DPE Oracle ID
1 | 166DB64C080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 54.3071533,25.5007026 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-071 | 25-PC--375 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040063 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.000X | Yes | Others | Periodic | e | Close | A10. Loose glands | A10. Tighten glands |  | 1 | 371.jpg 487.jpg 488.jpg | Yellow | 4 | Minor Repair Required | Equipment Isolation | Normal |  | Data Sheet 1 | Ashik Kasim | 2023-06-13 13:04 | A10. Done | 0 | 1.jpg | Green | Not Applicable | Good to Use | Equipment Isolation | Normal | Ashik Kasim | 2023-08-16 13:50 | N-B-10-W RISER ON B
2 | 7A95A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6183359,24.9752788 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-122 | 25-PC-376 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-072 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 | 2.jpg | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 2 | Ashik Kasim | 2023-06-13 10:33 |  | 0 | 2.jpg | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | G-B-12-O RISER ON B
3 | 786EB64C080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6183359,24.9752788 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-084 | 25-PC-402 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040215 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.000X | Yes | Others | Periodic | e | Close |  |  |  | 0 | 3.jpg | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 3 | Ashik Kasim | 2023-06-13 10:51 |  | 0 | 3.jpg | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | CCP2-JB-8-G RISER ON JB
4 | F78FA64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6183104,24.9753585 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-121 | 25-PC-402 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-065 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 | 4.jpg | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 4 | Ashik Kasim | 2023-06-13 10:59 |  | 0 | 4.jpg | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | CCP2-JB-8-G RISER ON CCP2
5 | 2494A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6183326,24.9751696 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-069 | 25-PC-371 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040243 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.000X | Yes | Others | Periodic | e | Close |  |  |  | 0 | 5.jpg | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 5 | Ashik Kasim | 2023-06-13 14:10 |  | 0 | 5.jpg | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | CCP1-B-8-G RISER ON B
6 | 377BA64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6183455,24.9751149 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-119 | 25-PC-372 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-081 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 | 6.jpg | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 6 | Ashik Kasim | 2023-06-13 14:21 |  | 0 | 6.jpg | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BZS660
7 | 4B94A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6183278,24.9750253 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-081 | 25-PC-396 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040360 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.000X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 7 | Ashik Kasim | 2023-06-13 14:34 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BZS610
8 | 1696A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6183533,24.9750543 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-083 | 25-PC-400 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040240 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.000X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 8 | Ashik Kasim | 2023-06-13 14:46 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BZS462 PR SENS ELMNT
9 | 0096A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6182972,24.9750341 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-118 | 25-PC-400 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-076 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 9 | Ashik Kasim | 2023-06-13 15:01 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-29 11:58 | BZS460
10 | 3E7BA64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 54.3071533,25.5007026 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-063 | 25-PC-360 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040364 | Electrical | Not Applicable | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.000X | Yes | Others | Periodic | e | Close | A4. Wrong fixing of IP washer | A4. Reposition IP washer with earth tag |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Others |  | Data Sheet 10 | Ashik Kasim | 2023-06-13 15:13 | A4. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Others | Ashik Kasim | 2023-08-15 09:38 | BZS450
11 | 2B93A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6183211,24.9750818 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-117 | 25-PC-360 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-075 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 11 | Ashik Kasim | 2023-06-13 15:23 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BZS360
12 | 977CA64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.618335,24.9750022 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-082 | 25-PC-398 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040250 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 12 | Ashik Kasim | 2023-06-14 08:38 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BZS310
13 | 407DA64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6183193,24.9749885 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-144 | 25-PC-398 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-060 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 13 | Ashik Kasim | 2023-06-14 08:49 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BZS262 PR SENS ELMNT
14 | E193A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6183015,24.9749632 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-163 | 25-PC-560 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040161 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 14 | Ashik Kasim | 2023-06-14 08:59 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BZS260
15 | 6694A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6183302,24.9749924 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-244 | 25-PC-560 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | Not visible | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 15 | Ashik Kasim | 2023-06-14 09:10 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BZS250
16 | 5E7EA64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15)/Stair Ways | 55.6182933,24.9749641 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-062 | 25-PC-358 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040244 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 16 | Ashik Kasim | 2023-06-14 09:21 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Not Applicable | Ashik Kasim | 2023-08-16 08:28 | BZS170
17 | 7095A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15)/Stair Ways | 55.6182805,24.9749865 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SFL-205 | 25-PC-358 | Flood Light | EATON | TMVA16LCY-UNV1-76-M20 | Not Available | Electrical | Not Applicable | Not Applicable | NEC | Class 1 Div 2 | ABCD | T4A | Not Available | +55 | UL | Not Available | Not applicable | Lighting | Periodic | d | Close | A10. Non certified blanking elements installed | A10. Replace with suitable type blanking elements | Certification verified | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Normal |  | Data Sheet 17 | Ashik Kasim | 2023-06-14 09:46 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Normal | Ashik Kasim | 2023-08-16 08:37 | BXY024 VALVE CONTROL,PNEUMATIC
18 | CB6BB64C080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15)/Stair Ways | 55.6183301,24.9750708 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-163A | 25-PC-559A | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040077 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 18 | Ashik Kasim | 2023-06-14 09:57 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BXT1 TRANSFORMER
19 | 6E94A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15)/Stair Ways | 55.6183598,24.9750423 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-245 | 25-PC-907 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-073 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 19 | Ashik Kasim | 2023-06-14 10:14 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BXSV660 SOLENOID VALVE
20 | 677BA64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6186403,24.9751309 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-132 | 25-PC-426 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-069 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | IBN | IECEx IBE 13.0004X | Yes | Lighting | Periodic | e | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 20 | Ashik Kasim | 2023-06-14 10:54 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Not Applicable | Ashik Kasim | 2023-08-16 13:47 | BXSV610 SOLENOID VALVE
21 | AA94A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6186509,24.9750813 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-096 | 25-PC-425 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040070 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 21 | Ashik Kasim | 2023-06-14 10:59 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BXSV560
22 | D66DB64C080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6185788,24.9750956 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-253 | 25-PC-781 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040252 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 22 | Ashik Kasim | 2023-06-14 11:09 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BXSV510
23 | 3A94A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6185557,24.9750813 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-148 | 25-PC-782 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-079 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 23 | Ashik Kasim | 2023-06-14 11:16 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-16 08:49 | BXSV460 SOLENOID VALVE
24 | 0A7CA64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6185546,24.9751071 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-252 | 25-PC-749 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040207 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 24 | Ashik Kasim | 2023-06-14 11:38 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BXSV410 SOLENOID VALVE
25 | A094A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6183556,24.9750738 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-147 | 25-PC-750 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-066 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 25 | Ashik Kasim | 2023-06-14 11:47 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BXSV360 SOLENOID VALVE
26 | 177DA64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6183556,24.9750738 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-250 | 25-PC-746 | Light Junction Box | Weidmuller | Klippon POK 161609Ex | XB-AE-A-040246 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 26 | Ashik Kasim | 2023-06-14 15:22 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BXSV310 SOLENOID VALVE
27 | A793A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6184694,24.9750874 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-145 | 25-PC-746 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-094 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 27 | Ashik Kasim | 2023-06-14 15:35 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-16 08:55 | BXSV260 SOLENOID VALVE
28 | C992A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6183448,24.9750765 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-251 | 25-PC-747 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040219 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 28 | Ashik Kasim | 2023-06-14 15:41 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BXSV210 SOLENOID VALVE
29 | 6C94A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6183138,24.9751105 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-146 | 25-PC-718 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-068 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 29 | Ashik Kasim | 2023-06-14 15:52 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BXSV160B SOLENOID VALVE
30 | D67CA64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6182805,24.9749865 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SFL-102 | 25-PC-386 | Flood Light | EATON | TMVA16LCY-UNV1-76-M20 | Not Available | Electrical | Not Applicable | Not Applicable | NEC | Class 1 Div 2 | ABCD | T4A | Not Available | +55 | UL | Not Available | Not applicable | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 30 | Ashik Kasim | 2023-06-15 08:26 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BXSV160A SOLENOID VALVE
31 | 387CA64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183448,24.9750765 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-076 | 25-PC-386 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040251 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 31 | Ashik Kasim | 2023-06-15 08:33 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BXSV020 SOLENOID VALVE
32 | 2495A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183448,24.9750765 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-077 | 25-PC-388 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040372 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 32 | Ashik Kasim | 2023-06-15 08:38 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BXSV005 SOLENOID VALVE
33 | 697CA64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183138,24.9751105 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-133 | 25-PC-388 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-034 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 33 | Ashik Kasim | 2023-06-15 08:58 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-16 13:48 | BXSE4 FLAME/SPARK ARRESTER
34 | 9B7CA64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183448,24.9750765 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-094 | 25-PC-422 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040359 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 34 | Ashik Kasim | 2023-06-15 09:07 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Not Applicable | Ashik Kasim | 2023-08-17 08:32 | BXSE3 FLAME/SPARK ARRESTER
35 | F990A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6185089,24.9751143 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-131 | 25-PC-422 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-025 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 35 | Ashik Kasim | 2023-06-15 09:20 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BXSE2 FLAME/SPARK ARRESTER
36 | 9F70B64C080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183448,24.9750765 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-075 | 25-PC-384 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040231 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 36 | Ashik Kasim | 2023-06-15 09:29 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BXSE1 FLAME/SPARK ARRESTER
37 | 847BA64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6185089,24.9751143 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-130 | 25-PC-384 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-035 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 37 | Ashik Kasim | 2023-06-15 09:41 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BXCV680 VLV CNTRL
38 | A393A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183448,24.9750765 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-092 | 25-PC-413 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040377 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 38 | Ashik Kasim | 2023-06-15 09:52 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BXCV660 VLV CNTRL
39 | D890A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6182805,24.9749865 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SFL-103 | 25-PC-418 | Flood Light | EATON | TMVA16LCY-UNV1-76-M20 | Not Available | Electrical | Not Applicable | Not Applicable | NEC | Class 1 Div 2 | ABCD | T4A | Not Available | +55 | UL | Not Available | Not applicable | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 39 | Ashik Kasim | 2023-06-15 09:56 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BXCV610 VLV CNTRL
40 | CA7AA64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183448,24.9750765 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-090 | 25-PC-414 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040200 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 40 | Ashik Kasim | 2023-06-15 10:01 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BXCV480 VLV CNTRL
41 | 9194A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6185089,24.9751143 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-129 | 25-PC-414 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-036 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 41 | Ashik Kasim | 2023-06-15 10:11 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BXCV460 VLV CNTRL
42 | 2693A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6185469,24.9751586 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-072 | 25-PC-378 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040366 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 42 | Ashik Kasim | 2023-06-15 10:23 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-17 08:38 | BXCV410 VLV CNTRL
43 | BF95A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6182805,24.9749865 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SFL-103 | 25-PC-378 | Flood Light | EATON | TMVA16LCY-UNV1-76-M20 | Not Available | Electrical | Not Applicable | Not Applicable | NEC | Class 1 Div 2 | ABCD | T4A | Not Available | +55 | UL | Not Available | Not applicable | Lighting | Periodic | d | Close | A10. Non certified blanking elements installed | A10. Replace with suitable type blanking elements | Certification verified | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 43 | Ashik Kasim | 2023-06-15 10:37 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-17 08:36 | BXCV380 VLV CNTRL
44 | F494A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6183138,24.9751105 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-149 | 25-PC-788 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-077 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 44 | Ashik Kasim | 2023-06-15 10:52 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BXCV360 VLV CNTRL
45 | 5094A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6183556,24.9750738 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-256 | 25-PC-788 | Light Junction Box | Weidmuller | Klippon POK 161609Ex | XB-AE-A-040224 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 45 | Ashik Kasim | 2023-06-15 10:56 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BXCV310 VLV CNTRL
46 | CB93A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6183138,24.9751105 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-150 | 25-PC-786 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-083 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 46 | Ashik Kasim | 2023-06-15 11:01 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BXCV280 VLV CNTRL
47 | DC94A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6183739,24.9751738 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-255 | 25-PC-786 | Light Junction Box | Weidmuller | Klippon POK 161609Ex | XB-AE-A-040275 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 47 | Ashik Kasim | 2023-06-15 11:05 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BXCV260 VLV CNTRL
48 | 7B93A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6183138,24.9751105 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-156 | 25-PC-798 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-078 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 48 | Ashik Kasim | 2023-06-15 11:08 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BXCV210 VLV CNTRL
49 | 2D94A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6183739,24.9751738 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-261 | 25-PC-798 | Light Junction Box | Weidmuller | Klippon POK 161609Ex | XB-AE-A-040261 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 49 | Ashik Kasim | 2023-06-15 11:12 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BXCV015 VLV CNTRL
50 | 8693A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.618545,24.9751254 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-151 | 25-PC-784 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-084 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 50 | Ashik Kasim | 2023-06-15 11:33 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-16 09:11 | BXCV013 VLV CNTRL
51 | A594A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6183739,24.9751738 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-254 | 25-PC-784 | Light Junction Box | Weidmuller | Klippon POK 161609Ex | XB-AE-A-040236 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 51 | Ashik Kasim | 2023-06-15 15:29 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BXCV011 VLV CNTRL
52 | 57B3AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.618545,24.9751254 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-155 | 25-PC-796 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-070 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 52 | Ashik Kasim | 2023-06-15 15:34 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BWHSP1 CONTROL STATION
53 | 2295A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6183739,24.9751738 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-260 | 25-PC-796 | Light Junction Box | Weidmuller | Klippon POK 161609Ex | XB-AE-A-040067 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 53 | Ashik Kasim | 2023-06-15 15:39 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BVP1068 VALVE,PLUG
54 | 137DA64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.618545,24.9751254 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-154 | 25-PC-794 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-074 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 54 | Ashik Kasim | 2023-06-15 15:44 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BVO4047 VALVE,GLOBE
55 | 097BA64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6183777,24.9753453 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-259 | 25-PC-794 | Light Junction Box | Weidmuller | Klippon POK 161609Ex | XB-AE-A-040199 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 55 | Ashik Kasim | 2023-06-15 15:58 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BVO4045 VALVE,GLOBE
56 | 5595A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6185089,24.9751143 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-128 | 25-PC-370 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-034 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 56 | Ashik Kasim | 2023-06-16 08:13 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BVO4043 VALVE,GLOBE
57 | D26CB64C080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183448,24.9750765 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-068 | 25-PC-370 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040205 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 57 | Ashik Kasim | 2023-06-16 08:17 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BVO4028 VALVE,GLOBE
58 | 5870B64C080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183448,24.9750765 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-088 | 25-PC-410 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040247 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 58 | Ashik Kasim | 2023-06-16 08:21 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BVO4026 VALVE,GLOBE
59 | B170B64C080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6185089,24.9751143 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-127 | 25-PC-410 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-071 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 59 | Ashik Kasim | 2023-06-16 08:31 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BVO1081 VALVE,GLOBE
60 | C893A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183448,24.9750765 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-089 | 25-PC-412 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040370 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 60 | Ashik Kasim | 2023-06-16 08:37 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-17 08:47 | BVO1069 VALVE,GLOBE
61 | 8795A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6182805,24.9749865 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SFL-104 | 25-PC-378 | Flood Light | EATON | TMVA16LCY-UNV1-76-M20 | Not Available | Electrical | Not Applicable | Not Applicable | NEC | Class 1 Div 2 | ABCD | T4A | Not Available | +55 | UL | Not Available | Not applicable | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | 1, M20 Dome Head Blanking Element Nos 1 | Data Sheet 61 | Ashik Kasim | 2023-06-16 08:42 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BVN1067 VALVE,NEEDLE
62 | B394A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183448,24.9750765 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-067 | 25-PC-368 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040227 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 62 | Ashik Kasim | 2023-06-16 08:51 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-17 09:00 | BVN1062 VALVE,NEEDLE
63 | 9070B64C080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6184928,24.9752726 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-126 | 25-PC-368 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-031 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 63 | Ashik Kasim | 2023-06-16 09:00 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-16 10:03 | BVN1033 VALVE,NEEDLE
64 | 917CA64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183448,24.9750765 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-087 | 25-PC-408 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040249 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 64 | Ashik Kasim | 2023-06-16 09:42 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  |  | BVN1032 VALVE,NEEDLE
65 | DAB5AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6184928,24.9752726 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-125 | 25-PC-408 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-026 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 65 | Ashik Kasim | 2023-06-16 09:19 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-16 10:08
66 | 3795A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183448,24.9750765 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-066 | 25-PC-366 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040203 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 66 | Ashik Kasim | 2023-06-16 09:40 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
67 | 5A95A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183926,24.975234 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-124 | 25-PC-366 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-042 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 67 | Ashik Kasim | 2023-06-16 09:32 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-16 10:22
68 | 2B91A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183448,24.9750765 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-086 | 25-PC-406 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040235 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 68 | Ashik Kasim | 2023-06-16 09:38 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-17 09:02
69 | 4B7DA64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183771,24.9752062 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-123 | 25-PC-406 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-039 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 69 | Ashik Kasim | 2023-06-16 09:47 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
70 | 0B7BA64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183896,24.975176 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-065 | 25-PC-364 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040216 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 70 | Ashik Kasim | 2023-06-16 09:51 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
71 | 316AB64C080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183742,24.9751617 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-143 | 25-PC-364 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-038 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 71 | Ashik Kasim | 2023-06-16 09:58 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-17 09:16
72 | CA7CA64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183783,24.9751362 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-099 | 25-PC-431 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040071 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 72 | Ashik Kasim | 2023-06-16 10:04 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
73 | E492A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183828,24.9751374 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-142 | 25-PC-432 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-028 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 73 | Ashik Kasim | 2023-06-16 10:18 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-17 09:18
74 | 4090A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183783,24.9751362 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-098 | 25-PC-430 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040204 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 74 | Ashik Kasim | 2023-06-16 10:42 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-17 09:26
75 | B594A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183828,24.9751374 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-138 | 25-PC-430 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-033 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 75 | Ashik Kasim | 2023-06-16 10:34 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-17 09:22
76 | 6370B64C080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183783,24.9751362 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-064 | 25-PC-362 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040234 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 76 | Ashik Kasim | 2023-06-16 10:41 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
77 | 4EB2AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183828,24.9751374 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-137 | 25-PC-43 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-029 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 77 | Ashik Kasim | 2023-06-16 10:53 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-17 09:41
78 | 2395A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183828,24.9751374 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-139 | 25-PC-382 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-041 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 78 | Ashik Kasim | 2023-06-16 11:14 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
79 | 5D7CA64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6184206,24.9751175 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-074 | 25-PC-381 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040064 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 79 | Ashik Kasim | 2023-06-16 11:06 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
80 | 7495A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6184815,24.9751402 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-093 | 25-PC-419 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040069 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 80 | Ashik Kasim | 2023-06-16 11:08 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
81 | 1693A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183828,24.9751374 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-140 | 25-PC-420 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-027 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 81 | Ashik Kasim | 2023-06-16 11:12 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-16 09:56
82 | 1594A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6185077,24.9751361 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-073 | 25-PC-380 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040313 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 82 | Ashik Kasim | 2023-06-16 11:18 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
83 | B193A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183828,24.9751374 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-141 | 25-PC-380 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-032 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 83 | Ashik Kasim | 2023-06-16 11:23 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-16 09:47
84 | 797BAB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6185077,24.9751361 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-257 | 25-PC-790 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040221 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 84 | Ashik Kasim | 2023-06-16 15:50 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
85 | 7E7BA64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.618545,24.9751254 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-152 | 25-PC-790 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-082 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 85 | Ashik Kasim | 2023-06-16 15:57 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
86 | 476EB64C080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183783,24.9751362 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-095 | 25-PC-424 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040197 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 86 | Ashik Kasim | 2023-06-19 08:04 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-17 09:51
87 | AA7BA64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183783,24.9751362 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-078 | 25-PC-390 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040065 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 87 | Ashik Kasim | 2023-06-19 08:09 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
88 | D47BA64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6184195,24.9750541 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-097 | 25-PC-428 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040254 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 88 | Ashik Kasim | 2023-06-19 08:13 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
89 | 437DA64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6184131,24.9750431 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-136 | 25-PC-428 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-040 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 89 | Ashik Kasim | 2023-06-19 08:31 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
90 | C28FA64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6184858,24.9750821 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-135 | 25-PC-390 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-036 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 90 | Ashik Kasim | 2023-06-19 08:28 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-17 09:46
91 | A7B5AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6184858,24.9750821 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-134 | 25-PC-424 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-030 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 91 | Ashik Kasim | 2023-06-19 08:41 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
92 | 8F7CA64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6184195,24.9750541 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-258 | 25-PC-792 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040270 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 92 | Ashik Kasim | 2023-06-19 08:45 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
93 | A490A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183828,24.9751374 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-153 | 25-PC-792 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-080 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 93 | Ashik Kasim | 2023-06-19 08:49 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
94 | 2793A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6183359,24.9752788 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-070 | 25-PC-402 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040214 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 94 | Ashik Kasim | 2023-06-19 09:02 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
95 | 9C94A64E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183828,24.9751374 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-153 | 25-PC-792 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-067 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 95 | Ashik Kasim | 2023-06-19 09:09 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
96 | C094A64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6183359,24.9752788 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-263 | 25-PC-802 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040307 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 96 | Ashik Kasim | 2023-06-19 09:20 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
97 | FC92A64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6183965,24.974787 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-247 | 25-PC-802 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-105 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 97 | Ashik Kasim | 2023-06-19 09:23 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
98 | D27AA64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6184695,24.9746887 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-262 | 25-PC-800 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-0403078 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 98 | Ashik Kasim | 2023-06-19 09:29 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
99 | 9994A64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6183965,24.974787 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-246 | 25-PC-800 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-122 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 99 | Ashik Kasim | 2023-06-19 09:34 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
100 | 0A95A64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6184784,24.9748077 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-264 | 25-PC-804 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040308 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 100 | Ashik Kasim | 2023-06-19 09:39 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
101 | 987AA64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6183965,24.974787 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-248 | 25-PC-804 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-110 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 101 | Ashik Kasim | 2023-06-19 09:44 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
102 | D795A64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6184603,24.9747949 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-267 | 25-PC-810 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040311 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 102 | Ashik Kasim | 2023-06-19 09:47 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
103 | 7A90A64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6184805,24.9749159 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-251 | 25-PC-810 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-119 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 103 | Ashik Kasim | 2023-06-19 09:51 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
104 | 2C6EB64C080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6184603,24.9747949 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-266 | 25-PC-808 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040310 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 104 | Ashik Kasim | 2023-06-19 10:50 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
105 | 5B7CA64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6183505,24.9748962 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-250 | 25-PC-808 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-106 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 105 | Ashik Kasim | 2023-06-19 10:55 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
106 | B295A64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.618515,24.9748573 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-273 | 25-PC-822 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040104 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 106 | Ashik Kasim | 2023-06-19 10:58 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
107 | 367CA64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6185912,24.9748674 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-257 | 25-PC-822 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-111 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 107 | Ashik Kasim | 2023-06-19 11:00 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
108 | AE92A64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.618543,24.9748908 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-268 | 25-PC-812 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040312 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 108 | Ashik Kasim | 2023-06-19 11:06 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
109 | DB95A64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6185501,24.9749817 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-252 | 25-PC-812 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-118 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 109 | Ashik Kasim | 2023-06-19 11:08 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
110 | 5F7CA64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.618543,24.9748908 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-272 | 25-PC-820 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040316 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 110 | Ashik Kasim | 2023-06-19 11:15 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
111 | 0F95A64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6185485,24.974985 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-256 | 25-PC-820 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-121 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 111 | Ashik Kasim | 2023-06-19 11:18 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
112 | 5E6FB64C080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.618543,24.9748908 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-271 | 25-PC-818 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040315 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 112 | Ashik Kasim | 2023-06-19 11:25 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
113 | 4192A64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6185485,24.974985 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-255 | 25-PC-818 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-124 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 113 | Ashik Kasim | 2023-06-19 11:30 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
114 | DF92A64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6184046,24.9749713 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-269 | 25-PC-814 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040302 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 114 | Ashik Kasim | 2023-06-19 11:33 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
115 | 2491A64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6185485,24.974985 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-253 | 25-PC-814 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-120 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 115 | Ashik Kasim | 2023-06-19 11:39 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
116 | EC7AA64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6184046,24.9749713 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-270 | 25-PC-816 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040314 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 116 | Ashik Kasim | 2023-06-19 15:38 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
117 | 7294A64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6185485,24.974985 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-254 | 25-PC-816 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-117 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 117 | Ashik Kasim | 2023-06-19 15:41 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-25 06:27
118 | BD93A64E080104E0 |  | Margham | Area 25 | Substation-Battery Room | 55.6139809,24.9723813 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XA-2597F | 25-CC-173 | Ex d- Battery Circuit Breaker Box | AD VIGANO | GUB 06 | 19.04.308 | Electrical | 2 | Gb | IEC | Ex d | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 09 ATEX 0050X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 118 | Ashik Kasim | 2023-06-21 09:47 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
119 | 2C7CA64E080104E0 |  | Margham | Area 25 | Substation-Battery Room | 55.6139809,24.9723813 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XA-2597E | 25-CC-172 | Ex d- Battery Circuit Breaker Box | AD VIGANO | GUB 06 | 19.04.307 | Electrical | 2 | Gb | IEC | Ex d | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 09 ATEX 0050X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 119 | Ashik Kasim | 2023-06-21 09:53 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
120 | 967CA64E080104E0 |  | Margham | Area 25 | Substation-Battery Room | 55.6139809,24.9723813 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XA-2597H | 25-CC-175 | Ex d- Battery Circuit Breaker Box | AD VIGANO | GUB 05 | 19.04.305 | Electrical | 2 | Gb | IEC | Ex d | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 09 ATEX 0050X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 120 | Ashik Kasim | 2023-06-21 09:59 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
121 | 9D94A64E080104E0 |  | Margham | Area 25 | Substation-Battery Room | 55.617363,24.9748946 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XA-2597G | 25-CC-174 | Ex d- Battery Circuit Breaker Box | AD VIGANO | GUB 05 | 19.04.306 | Electrical | 2 | Gb | IEC | Ex d | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 09 ATEX 0050X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 121 | Ashik Kasim | 2023-06-21 10:08 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
122 | C293A64E080104E0 |  | Margham | Area 25 | Substation-Battery Room | 55.617363,24.9748946 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XL-2574D | FA/XL-25-2574D/25-XL-2574D | BEACON LIGHT | e2S European Safety System Ltd | BExBG05D-P | 20/1DB12018979 | Electrical | 2 | Gb | IEC | Ex d | IIC | T4 | Not Available | -50 +70 | KEMA | KEMA 00ATEX2006X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 122 | Ashik Kasim | 2023-06-21 10:34 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
123 | 8893A64E080104E0 |  | Margham | Area 25 | Substation-Battery Room | 55.617363,24.9748946 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XL-2573D | FA/XL-25-2573D/25-XL-2573D | BEACON SOUNDER | e2S European Safety System Ltd | BExS110D-R | 20/1S22021327 | Electrical | 2 | Gb | IEC | Ex d | IIC | T4 | Not Available | -50 +70 | KEMA | KEMA 00ATEX6312X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 123 | Ashik Kasim | 2023-06-21 10:34 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
124 | 1896A64E080104E0 |  | Margham | Area 25 | Substation-Battery Room | 55.617363,24.9748946 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MRU-2594 | FA/25-MRU-2564/AI/25-MCP-2564 | Manual Call Point | Kidde | 84-100004-001 | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 | BCD | Not Available | Not Available | Not Available | UL | Not Available | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 124 | Ashik Kasim | 2023-06-21 10:46 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
125 | B47AA64E080104E0 |  | Margham | Area 25 | Substation-Battery Room | 55.6168923,24.9750624 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MCP-2566 | FA/25-MCP-2566/AI/25-MCP-2566/AI | Manual Call Point | Kidde | 84-100004-001 | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 | BCD | Not Available | Not Available | Not Available | UL | Not Available | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 125 | Ashik Kasim | 2023-06-21 10:54 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
126 | 7C95A64E080104E0 |  | Margham | Area 25 | Substation-Battery Room | 55.6172616,24.9750263 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SSC-27 | 25-PC-929 | Power Socket-220v/250v | Marechal Electric France | DXA1 2914015 | Not Available | Electrical | 2 | Gb | IEC | Ex de | IIC | T5 | IP66/67 | -55 +60 | LCIE | LCIE15ATEX3033X | Yes | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable | 1, Earth Cable Meters: 10 | Data Sheet 126 | Ashik Kasim | 2023-06-21 11:06 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable
127 | 6B94A64E080104E0 |  | Margham | Area 25 | Substation-Battery Room | 55.6172616,24.9750263 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SSC-26 | 25-PC-928 | Power Socket-220v/250v | Marechal Electric France | DXA1 2914015 | Not Available | Electrical | 2 | Gb | IEC | Ex de | IIC | T5 | IP66/67 | -55 +60 | LCIE | LCIE15ATEX3033X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 127 | Ashik Kasim | 2023-06-21 11:24 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
128 | 1095A64E080104E0 |  | Margham | Area 25 | Substation-Battery Room | 55.6172616,24.9750263 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SIP-2504 | FA/25-SIP-2504/AO/25-SIP-2504 | NOVEC Switch | EATON | GHG44 | Not Available | Electrical | 2 | Not Available | IEC | Ex de | IIC | T6 | Not Available | Not available | PTB | PTB 99 ATEX 1044 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 128 | Ashik Kasim | 2023-06-21 11:26 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
129 | B593A64E080104E0 |  | Margham | Area 25 | Substation-Battery Room | 55.6172616,24.9750263 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-DB-001 | 25-PLF-080 | Light Switch | TECHNOR ITALSMEA | CPSG-26/EFSRC-220 | 20P0092440010 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 129 | Ashik Kasim | 2023-06-21 11:35 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
130 | 3995A64E080104E0 |  | Margham | Area 25 | Substation-Battery Room | 55.6172616,24.9750263 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-DC-BAT-TS-001 | 25-CC-178 | Temperature Sensor -DC UPS Battery Rack A | BARTEC FEAM | GUAC-16 | 10/19 | Electrical | 2 | Gb | IEC | Ex d | IIC | T6 | IP66 | -60 +60 | INERIS | INERIS 03ATEX0048X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 130 | Ashik Kasim | 2023-06-21 11:44 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
131 | 3B94A64E080104E0 |  | Margham | Area 25 | Substation-Battery Room | 55.6172616,24.9750263 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-DC-BAT-TS-002 | 25-CC-179 | Temperature sensor - DC UPS Battery Rack B | BARTEC FEAM | GUAC-16 | 10/19 | Electrical | 2 | Gb | IEC | Ex d | IIC | T6 | IP66 | -60 +60 | INERIS | INERIS 03ATEX0048X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 131 | Ashik Kasim | 2023-06-21 11:51 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
132 | F296A64E080104E0 |  | Margham | Area 25 | Substation-Battery Room | 55.6172616,24.9750263 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AC-BAT-TS-001 | 25-CC-176 | Temperature Sensor - AC UPS Battery Rack A | BARTEC FEAM | GUAC-16 | 10/19 | Electrical | 2 | Gb | IEC | Ex d | IIC | T6 | IP66 | -60 +60 | INERIS | INERIS 03ATEX0048X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 132 | Ashik Kasim | 2023-06-21 11:56 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
133 | D695A64E080104E0 |  | Margham | Area 25 | Substation-Battery Room | 55.6178434,24.9751443 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AC-BAT-TS-002 | 25-CC-177 | Temperature Sensor - AC UPS Battery Rack B | BARTEC FEAM | GUAC-16 | 10/19 | Electrical | 2 | Gb | IEC | Ex d | IIC | T6 | IP66 | -60 +60 | INERIS | INERIS 03ATEX0048X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 133 | Ashik Kasim | 2023-06-21 11:59 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
134 | 4B95A64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6172333,24.9749038 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-298 | 25-PC-859 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040139 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 134 | Ashik Kasim | 2023-06-21 15:50 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-22 08:18
135 | 307CA64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6172243,24.9749111 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-241 | 25-PC-716 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040141 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 135 | Ashik Kasim | 2023-06-21 15:52 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-22 08:25
136 | 9969B64C080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6172185,24.9748724 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-BFL-404 | 25-PC-710 | Flood Light | EATON | FMVA16LCY-UNV1-76-M20 | Not Available | Electrical | Not Applicable | Not Applicable | NEC | Class 1 Div 2 | ABCD | T4A | Not Available | +55 | UL | Not Available | Not applicable | Lighting | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 136 | Ashik Kasim | 2023-06-21 15:56 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-22 09:15
137 | 4C95A64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6172339,24.9748716 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-238 | 25-PC-902 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040173 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 137 | Ashik Kasim | 2023-06-21 16:00 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-22 09:17
138 | EC93A64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6171388,24.9748558 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-WLF-030 | 25-PC-712 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-032 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 138 | Ashik Kasim | 2023-06-21 16:04 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-22 09:40
139 | 9D69B64C080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6172339,24.9748716 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-239 | 25-PC-711 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040144 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 139 | Ashik Kasim | 2023-06-21 16:07 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-22 09:20
140 | 988FA64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6171604,24.9748045 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-296 | 25-PC-855 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040166 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 140 | Ashik Kasim | 2023-06-21 16:09 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-22 09:34
141 | 2D91A64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6171468,24.9748155 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-BFL-403 | 25-PC-855 | Flood Light | EATON | FMVA16LCY-UNV1-76-M20 | Not Available | Electrical | Not Applicable | Not Applicable | NEC | Class 1 Div 2 | ABCD | T4A | Not Available | +55 | UL | Not Available | Not applicable | Lighting | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 141 | Ashik Kasim | 2023-06-21 16:14 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-22 09:32
142 | E792A64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6171604,24.9748045 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-242 | 25-PC-717 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040179 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 142 | Ashik Kasim | 2023-06-21 16:19 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
143 | 6369B64C080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6171604,24.9748045 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-243 | 25-PC-719 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040132 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 143 | Ashik Kasim | 2023-06-22 08:05 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
144 | F294A64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6171604,24.9748045 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-392 | 25-PC-854 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040122 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 144 | Ashik Kasim | 2023-06-22 08:09 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
145 | 9892A64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6172118,24.9750713 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-WLF-032 | 25-PC-808 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-044 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable | 1, Earth cable Meters: 5 | Data Sheet 145 | Ashik Kasim | 2023-06-22 08:28 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-23 14:21
146 | FA90A64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6171485,24.9751359 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-244 | 25-PC-722 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040283 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 146 | Ashik Kasim | 2023-06-22 08:21 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-23 05:49
147 | 9D6EB64C080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6171341,24.9751216 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-WLF-033 | 25-PC-857 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-037 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 147 | Ashik Kasim | 2023-06-22 08:26 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-23 10:49
148 | EB92A64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.617126,24.9751233 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-297 | 25-PC-719 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040387 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 148 | Ashik Kasim | 2023-06-22 08:41 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
149 | C57CA64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6172616,24.9750263 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SOC-008 | 25-PC-917 | Power Socket-220v/250v | Marechal Electric France | DXA1 2914015 | Not Available | Electrical | 2 | Gb | IEC | Ex de | IIC | T5 | IP66/67 | -55 +60 | LCIE | LCIE15ATEX3033X | Yes | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable | 1, Earth cable Meters: 5 | Data Sheet 149 | Ashik Kasim | 2023-06-22 08:36 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-23 11:04
150 | 0C95A64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6171284,24.9751204 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SJB-04 | 25-PC-915 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040298 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 150 | Ashik Kasim | 2023-06-22 08:44 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
151 | F5B2AB4E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.617126,24.9751233 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-301 | 25-PC-858 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040273 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 151 | Ashik Kasim | 2023-06-22 08:50 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
152 | F490A64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.617078,24.9751169 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-WLF-034 | 25-PC-865 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-004 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable | 1, Earth cable Meters: 5 | Data Sheet 152 | Ashik Kasim | 2023-06-22 08:56 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-23 10:08
153 | F492A64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.617018,24.9751307 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-304 | 25-PC-860 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040259 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 153 | Ashik Kasim | 2023-06-22 08:59 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-23 05:44
154 | 4793A64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6170139,24.9751257 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-BFL-405 | 25-PC-714 | Flood Light | EATON | FMVA16LCY-UNV1-76-M20 | Not Available | Electrical | Not Applicable | Not Applicable | NEC | Class 1 Div 2 | ABCD | T4A | Not Available | +55 | UL | Not Available | Not applicable | Lighting | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 154 | Ashik Kasim | 2023-06-22 09:02 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-23 09:14
155 | 5995A64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6170222,24.9751404 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-240 | 25-PC-871 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040124 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 155 | Ashik Kasim | 2023-06-22 09:04 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
156 | 5F80A64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6170136,24.9751333 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-245 | 25-PC-737 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040138 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 156 | Ashik Kasim | 2023-06-22 09:08 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
157 | C18FA64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.617078,24.9751169 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-WLF-035 | 25-PC-871 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-029 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable | 1, Earth cable Meters: 5 | Data Sheet 157 | Ashik Kasim | 2023-06-22 09:15 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-23 09:38
158 | 2093A64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6172616,24.9750263 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SOC-007 | 25-PC-916 | Power Socket-220v/250v | Marechal Electric France | DXA1 2914015 | Not Available | Electrical | 2 | Gb | IEC | Ex de | IIC | T5 | IP66/67 | -55 +60 | LCIE | LCIE15ATEX3033X | Yes | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable | 1, Earth cable Meters: 5 | Data Sheet 158 | Ashik Kasim | 2023-06-22 09:18 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-23 09:07
159 | A794A64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6170136,24.9751333 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-300 | 25-PC-864 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040291 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 159 | Ashik Kasim | 2023-06-22 09:33 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
160 | AA95A64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6169794,24.9751077 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-WLF-036 | 25-PC-863 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-038 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable | 1, Earth cable Meters: 5 | Data Sheet 160 | Ashik Kasim | 2023-06-22 09:36 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-23 08:54
161 | F993A64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6169782,24.9750751 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-246 | 25-PC-737 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040329 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 161 | Ashik Kasim | 2023-06-22 09:38 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
162 | E392A64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6169764,24.9750099 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-303 | 25-PC-866 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040349 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 162 | Ashik Kasim | 2023-06-22 09:49 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
163 | 916CB64C080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6169794,24.9751077 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-WLF-037 | 25-PC-869 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-041 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable | 1, Earth cable Meters: 5 | Data Sheet 163 | Ashik Kasim | 2023-06-22 09:56 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-23 05:38
164 | B294A64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6169727,24.974846 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-WLF-038 | 25-PC-872 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-039 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable | 1, Earth cable Meters: 5 | Data Sheet 164 | Ashik Kasim | 2023-06-22 10:00 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-22 10:45
165 | B77BA64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6169709,24.9748415 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-305 | 25-PC-868 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040335 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 165 | Ashik Kasim | 2023-06-22 10:05 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-22 11:02
166 | 0E96A64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6169709,24.9748415 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-306 | 25-PC-903 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040290 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 166 | Ashik Kasim | 2023-06-22 10:08 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
167 | 047CA64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6169709,24.9748415 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-307 | 25-PC-899 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040171 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 167 | Ashik Kasim | 2023-06-22 10:10 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
168 | A294A64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6169709,24.9748415 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-236 | 25-PC-870 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040398 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 168 | Ashik Kasim | 2023-06-22 10:13 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-22 10:36
169 | 586FB64C080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6171065,24.9747012 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-BFL-401 | 25-PC-706 | Flood Light | EATON | NFMVA25LCY/UNV1-76-M20 | Not Available | Electrical | 3 | Gc | IEC | Ex ec | IIC | T4 | IP66 | -40 +55 | DEMKO | DEMKO 15 ATEX 1377X/1383 | Yes | Lighting | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 169 | Ashik Kasim | 2023-06-22 10:23 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-22 10:38
170 | 6091A64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6171065,24.9747012 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-BFL-402 | 25-PC-708 | Flood Light | EATON | NFMVA25LCY/UNV1-76-M20 | Not Available | Electrical | 3 | Gc | IEC | Ex ec | IIC | T4 | IP66 | -40 +55 | DEMKO | DEMKO 15 ATEX 1377X/1383 | Yes | Lighting | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 170 | Ashik Kasim | 2023-06-22 10:26 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-22 10:16
171 | 978FA64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.617113,24.9747247 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-237 | 25-PC-707 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040146 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 171 | Ashik Kasim | 2023-06-22 10:30 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-22 10:13
172 | F88FA64E080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6171165,24.9747596 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2588E | FA/25-MB-2508/25-AE-2588E | Gas Detector | Crowcon | XIQ-ZZ-S1-011-Z-R-A | W322590/01-001 | Instrumentation | 2 | Gb | IEC | Ex db ia | IIC | T4 | Not Available | Not available | Baseefa | Baseefa 14ATEX0012X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 172 | Ashik Kasim | 2023-06-22 10:45 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
173 | C56EB64C080104E0 |  | Margham | Area 25 | Substation Building Top | 55.6171165,24.9747596 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2588F | FA/25-MB-2508/25-AE-2588F | Gas Detector | Crowcon | XIQ-ZZ-S1-011-Z-R-A | W322590/01-002 | Instrumentation | 2 | Gb | IEC | Ex db ia | IIC | T4 | Not Available | Not available | Baseefa | Baseefa 14ATEX0012X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 173 | Ashik Kasim | 2023-06-22 11:24 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
174 | 027DA64E080104E0 |  | Margham | Area 25 | Substation Building-Outdoor | 55.6172393,24.9749766 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MCP-2565 | FA/25-FAECP-01/25-MCP-2565/A1 | Manual Call Point | Kidde | 84-100004-001 | Not available | Instrumentation | Not Available | Not Available | NEC | Class 1 | BCD | Not Available | Not Available | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 174 | Ashik Kasim | 2023-06-22 15:36 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
175 | 918FA64E080104E0 |  | Margham | Area 25 | Substation Building-Outdoor | 55.6172393,24.9749766 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MCP-2573 | FA/25-MCP-2573/AI/25-AE-25761 | Manual Call Point | Kidde | 84-100004-001 | Not available | Instrumentation | Not Available | Not Available | NEC | Class 1 | BCD | Not Available | Not Available | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 175 | Ashik Kasim | 2023-06-22 15:38 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
176 | 7B7BA64E080104E0 |  | Margham | Area 25 | Substation Building-Outdoor | 55.6171637,24.9747733 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MCP-2562 | FA/25-MRU-2562/AI/25-ABT-2566/AI | Manual Call Point | Kidde | 84-100004-001 | Not available | Instrumentation | Not Available | Not Available | NEC | Class 1 | BCD | Not Available | Not Available | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 176 | Ashik Kasim | 2023-06-22 15:44 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
177 | 3B6EB64C080104E0 |  | Margham | Area 25 | Substation Building-Outdoor | 55.617046,24.9748759 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MCP-2561 | FA/25-TM-2561/AO/25-MRU-2561/A1 | Manual Call Point | Kidde | 84-100004-001 | Not available | Instrumentation | Not Available | Not Available | NEC | Class 1 | BCD | Not Available | Not Available | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 177 | Ashik Kasim | 2023-06-22 15:48 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
178 | 507DA64E080104E0 |  | Margham | Area 25 | Substation-Outdoor/Transformer Bay | 55.6169035,24.9750344 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SOC-001 | 25-PC-908 | Power Socket-220v/250v | Marechal Electric France | DXA1 2914015 | Not Available | Electrical | 2 | Gb | IEC | Ex de | IIC | T5 | IP66/67 | -55 +60 | LCIE | LCIE15ATEX3033X | Yes | Others | Periodic | d | Close | B6. Earth cable not installed A10. Loose glands | B6. Install earth cable A10. Tighten glands |  | 2 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable | 1, Earth cable Meters: 5 | Data Sheet 178 | Ashik Kasim | 2023-06-23 15:41 | B6. Done A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-28 16:03
179 | 2F95A64E080104E0 |  | Margham | Area 25 | Substation-Outdoor/Transformer Bay | 55.617046,24.9748759 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MCP-2571 | FA/25-MCP-2571/A1/25-AE-2587C | Manual Call Point | Kidde | 84-100004-001 | Not available | Instrumentation | Not Available | Not Available | NEC | Class 1 | BCD | Not Available | Not Available | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 179 | Ashik Kasim | 2023-06-23 15:40 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
180 | D793A64E080104E0 |  | Margham | Area 25 | Substation-Outdoor/Transformer Bay | 55.6168997,24.9749287 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SOC-002 | 25-PC-909 | Power Socket-220v/250v | Marechal Electric France | DXA1 2914015 | Not Available | Electrical | 2 | Gb | IEC | Ex de | IIC | T5 | IP66/67 | -55 +60 | LCIE | LCIE15ATEX3033X | Yes | Others | Periodic | d | Close | B6. Earth cable not installed A10. Loose glands | B6. Install earth cable A10. Tighten glands |  | 2 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable | 1, Earth cable Meters: 5 | Data Sheet 180 | Ashik Kasim | 2023-06-23 15:45 | B6. Done A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-28 16:05
181 | 717BA64E080104E0 |  | Margham | Area 25 | Substation-Outdoor/Transformer Bay | 55.6168997,24.9749287 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SOC-003 | 25-PC-910 | Power Socket-220v/250v | Marechal Electric France | DXA1 2914015 | Not Available | Electrical | 2 | Gb | IEC | Ex de | IIC | T5 | IP66/67 | -55 +60 | LCIE | LCIE15ATEX3033X | Yes | Others | Periodic | d | Close | B6. Earth cable not installed A10. Loose glands | B6. Install earth cable A10. Tighten glands |  | 2 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable | 1, Earth cable Meters: 5 | Data Sheet 181 | Ashik Kasim | 2023-06-23 15:47 | B6. Done A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-28 16:16
182 | 1C7DA64E080104E0 |  | Margham | Area 25 | Substation-Outdoor/Transformer Bay | 55.617046,24.9748759 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MCP-2572 | FA/25-MCP-2572/A1/25-MB-2504 | Manual Call Point | Kidde | 84-100004-001 | Not available | Instrumentation | Not Available | Not Available | NEC | Class 1 | BCD | Not Available | Not Available | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 182 | Ashik Kasim | 2023-06-23 16:00 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
183 | 8258AB4E080104E0 |  | Margham | Area 20 | Train-1/20C101SS Seal Oil Console | 55.6139809,24.9723813 | Zone 2 | IIB | T3 | Not Available | EE-20-A0-654-01 |  | 20-ITB-07 | 20-ITB-07-1403 | Junction Box | ABTECH | SX.1.5.140 | 219850 | Instrumentation | 2 | Not Available | IEC | Ex e | IIC | T5 | IP66 | Not Available | SIRA | SIRA99ATEX3171 | Not Applicable | Others | Periodic | e | Close | A4. IP washer missing C2. Accumulation of dust and dirt | A4. Install IP washer C2. Remove the dust and dirt |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation |  |  | Data Sheet 183 | Ashik Kasim | 2023-06-24 08:53 | A4. Pending C2. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation
184 | 0A60AB4E080104E0 |  | Margham | Area 20 | Train-1/20C101SS Seal Oil Console | 55.6139809,24.9723813 | Zone 2 | IIB | T3 | Not Available | EE-20-A0-654-01 |  | 20-ITB-06 | 20-ITB-07-1431 | Junction Box. | ABTECH | SX.1.5.140 | 219843 | Instrumentation | 2 | Not Available | IEC | Ex e | IIC | T5 | IP66 | Not Available | SIRA | SIRA99ATEX3171 | Not Applicable | Others | Periodic | e | Close | A4. IP washer missing C2. Accumulation of dust and dirt A10. Bolts missing | A4. Install IP washer C2. Remove the dust and dirt A10. Fix with manufacture recommended bolts | open entry | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation |  | 1, 1/2"NPT IP WASHER Nos: 16 2, Bolt 6mm Nos: 1 | Data Sheet 184 | Ashik Kasim | 2023-06-24 09:22 | A4. Pending C2. Pending A10. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation
185 | DC5BAB4E080104E0 |  | Margham | Area 20 | Train-1/20C101SS Seal Oil Console | 55.6198765,24.9774929 | Zone 2 | IIB | T3 | Not Available | EE-20-A0-654-01 |  | Not Available | 20-CJB-20-1411 | Junction Box | ASP | EJB-51 | Not Available | Electrical | Not Available | Not Available | IEC | Ex d | IIB | T5 | IP54 | Not Available | INIEX | INIEX80.103.044 | Not Applicable | Others | Periodic | d | Close | C2. Accumulation of dust and dirt A6. Equipment id not available B6. Earth cable not installed | C2. Remove the dust and dirt A6. Fix equipment id B6. Install earth cable |  | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation |  | 1, Earth Cable Meters : 2 | Data Sheet 185 | Ashik Kasim | 2023-06-24 09:24 | C2. Pending A6. Pending B6. Pending | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation
186 | AB5AAB4E080104E0 |  | Margham | Area 20 | Train-1/20C101DS Seal Oil Console | 55.6198765,24.9774929 | Zone 2 | IIB | T3 | Not Available | EE-20-A0-654-01 |  | 20-ITB-10 | 20-ITB-10-1430 | Junction Box | ABTECH | SX.1.5.140 | 219835 | Instrumentation | 2 | Not Available | IEC | Ex e | IIC | T5 | IP66 | Not Available | SIRA | SIRA99ATEX3171 | Not Applicable | Others | Periodic | e | Close | A4. IP washer missing C2. Accumulation of dust and dirt | A4. Install IP washer C2. Remove the dust and dirt |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation |  |  | Data Sheet 186 | Ashik Kasim | 2023-06-24 09:30 | A4. Pending C2. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation
187 | D95DAB4E080104E0 |  | Margham | Area 20 | Train-1/20C101DS Seal Oil Console | 55.6182964,24.9771797 | Zone 2 | IIB | T3 | Not Available | EE-20-A0-654-01 |  | 20-ITB-03 | 20-ITB-03-1420 | Junction Box | ABTECH | SX.1.5.140 | 219837 | Instrumentation | 2 | Not Available | IEC | Ex e | IIC | T5 | IP66 | Not Available | SIRA | SIRA99ATEX3171 | Not Applicable | Others | Periodic | e | Close | A4. IP washer missing C2. Accumulation of dust and dirt A6. Equipment id not available | A4. Install IP washer C2. Remove the dust and dirt A6. Fix equipment id |  | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation |  | 1, M20 IP Washer Nos: 16 | Data Sheet 187 | Ashik Kasim | 2023-06-24 10:48 | A4. Pending C2. Pending A6. Pending | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation
188 | BB5DAB4E080104E0 |  | Margham | Area 20 | Train-1/20C101DS Seal Oil Console | 55.6198765,24.9774929 | Zone 2 | IIB | T3 | Not Available | EE-20-A0-654-01 |  | 20-C-101 | 20-CJB-20-1411 | Junction Box | ASP | EJB-54 | Not Available | Electrical | Not Available | Not Available | IEC | Ex d | IIB | T5 | IP54 | Not Available | INIEX | INIEX80.103.044 | Not Applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 188 | Ashik Kasim | 2023-06-24 10:02 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
189 | 7A5CAB4E080104E0 |  | Margham | Area 20 | Train-1/Compressor BLDG | 55.6186113,24.9772081 | Zone 2 | IIB | T3 | Not Available | EE-20-A0-654-01 |  | 20--BD-1-DR-6 | Not Available | Junction Box / Roll-Up-Door 6 | Nelson Electric | OF8106 | WA161M7 | Electrical | Not Available | Not Available | NEC | Class 1 | D | Not Available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | C2. Accumulation of dust and dirt A6. Circuit id not available B6. Earth cable not installed | C2. Remove the dust and dirt A6. Fix circuit id B6. Install earth cable |  | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation |  |  | Data Sheet 189 | Ashik Kasim | 2023-06-24 10:28 | C2. Pending A6. Pending B6. Pending | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation
190 | F05DAB4E080104E0 |  | Margham | Area 20 | Train-1/Compressor BLDG | 55.618623,24.9771465 | Zone 2 | IIB | T3 | Not Available | EE-20-A0-654-01 |  | 20--BD1-DR-6 | Not Available | On/Off Switch/ Roll-Up-Door 6 | Telemecanique | Not Available | Not Available | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | C2. Accumulation of dust and dirt B6. Earth cable not installed A1. Non conformant equipment A6. Circuit id not available A10. Damaged blanking elements | C2. Remove the dust and dirt B6. Install earth cable A1. Replace equipment unless proven otherwise A6. Fix circuit id A10. Replace with suitable type blanking elements |  | 5 |  | Red | 2 | Major Repair Required | Equipment Isolation |  | 1, 3/4" Stop plugs Nos : 1 | Data Sheet 190 | Ashik Kasim | 2023-06-24 10:24 | C2. Pending B6. Pending A1. Pending A6. Pending A10. Pending | 5 |  | Red | 2 | Major Repair Required | Equipment Isolation
191 | B76EB64C080104E0 |  | Margham | Area 20 | Train-1/Compressor BLDG | 55.6184872,24.977427 | Zone 2 | IIB | T3 | Not Available | EE-20-A0-654-01 |  | 20--BD-1-DR-9 | Not Available | Junction Box / Roll-Up-Door 9 | Nelson Electric | OF8106 | WA161M7 | Electrical | Not Available | Not Available | NEC | Class 1 | D | Not Available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed | A6. Fix circuit id B6. Install earth cable |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation |  |  | Data Sheet 191 | Ashik Kasim | 2023-06-24 10:39 | A6. Pending B6. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation
192 | 8357AB4E080104E0 |  | Margham | Area 20 | Train-1/Compressor BLDG | 55.6185334,24.9775461 | Zone 2 | IIB | T3 | Not Available | EE-20-A0-654-01 |  | 20--BD1-DR-9 | Not Available | On/Off Switch/ Roll-Up-Door 9 | Telemecanique | Not Available | Not Available | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed A1. Non conformant equipment A6. Circuit id not available A10. Damaged blanking elements | B6. Install earth cable A1. Replace equipment unless proven otherwise A6. Fix circuit id A10. Replace with suitable type blanking elements |  | 4 |  | Red | 2 | Major Repair Required | Equipment Isolation |  | 1, 3/4" Stop plugs Nos: 1 | Data Sheet 192 | Ashik Kasim | 2023-06-24 10:44 | B6. Pending A1. Pending A6. Pending A10. Pending | 4 |  | Red | 2 | Major Repair Required | Equipment Isolation
193 | B658AB4E080104E0 |  | Margham | Area 20 | Train-1/Compressor BLDG | 55.6184872,24.977427 | Zone 2 | IIB | T3 | Not Available | EE-20-A0-654-01 |  | 20--BD-1-DR-7 | Not Available | Junction Box / Roll-Up-Door 7 | Nelson Electric | OF8106 | WA161M7 | Electrical | Not Available | Not Available | NEC | Class 1 | D | Not Available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed | A6. Fix circuit id B6. Install earth cable |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 193 | Ashik Kasim | 2023-06-24 10:54 | A6. Pending B6. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation
194 | FD5AAB4E080104E0 |  | Margham | Area 20 | Train-1/Compressor BLDG | 55.6183762,24.9779353 | Zone 2 | IIB | T3 | Not Available | EE-20-A0-654-01 |  | 20--BD1-DR-7 | Not Available | On/Off Switch/ Roll-Up-Door 7 | Telemecanique | Not Available | Not Available | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed A1. Non conformant equipment A6. Equipment id not available A6. Circuit id not available A10. Bolts missing | B6. Install earth cable A1. Replace equipment unless proven otherwise A6. Fix equipment id A6. Fix circuit id A10. Fix with manufacture recommended bolts |  | 5 |  | Red | 2 | Major Repair Required | Equipment Isolation |  | 1, 3/4" Stop plugs Nos: 1 | Data Sheet 194 | Ashik Kasim | 2023-06-24 10:58 | B6. Pending A1. Pending A6. Pending A6. Pending A10. Pending | 5 |  | Red | 2 | Major Repair Required | Equipment Isolation
195 | A95CAB4E080104E0 |  | Margham | Area 20 | Train-1/Outdoor Near Vessel-101 | 55.6198765,24.9774929 | Zone 2 | IIB | T3 | Not Available | EE-20-A0-654-01 |  | 20-ITB-14 | 20-ITB-14-1406 | Junction Box | ABTECH | SX.1.5.140 | 219831 | Instrumentation | 2 | Not Available | IEC | Ex e | IIC | T5 | IP66 | Not Available | SIRA | SIRA99ATEX3171 | Not Applicable | Others | Periodic | e | Close | A4. IP washer missing C2. Accumulation of dust and dirt | A4. Install IP washer C2. Remove the dust and dirt |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation |  |  | Data Sheet 195 | Ashik Kasim | 2023-06-24 11:25 | A4. Pending C2. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation
196 | 985CAB4E080104E0 |  | Margham | Area 20 | Train-1/Outdoor Near Vessel-101 | 55.6188081,24.9770286 | Zone 2 | IIB | T3 | Not Available | EE-20-A0-654-01 |  | 20-ITB-11 | 20-ITB-11-1432 | Junction Box | ABTECH | SX.1.5.140 | 219854 | Instrumentation | 2 | Not Available | IEC | Ex e | IIC | T5 | IP66 | Not Available | SIRA | SIRA99ATEX3171 | Not Applicable | Others | Periodic | e | Close | A4. IP washer missing | A4. Install IP washer |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation |  |  | Data Sheet 196 | Ashik Kasim | 2023-06-24 11:29 | A4. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation
197 | 755CAB4E080104E0 |  | Margham | Area 20 | Train-1/Outdoor Near Vessel-101 | 55.6187245,24.9770004 | Zone 2 | IIB | T3 | Not Available | EE-20-A0-654-01 |  | 20-ITB-20 | 20-ITB-20-1418 | Junction Box | ABTECH | SX.1.5.140 | 219836 | Instrumentation | 2 | Not Available | IEC | Ex e | IIC | T5 | IP66 | Not Available | SIRA | SIRA99ATEX3171 | Not Applicable | Others | Periodic | e | Close | A4. IP washer missing | A4. Install IP washer |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation |  |  | Data Sheet 197 | Ashik Kasim | 2023-06-24 11:33 | A4. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation
198 | 8458AB4E080104E0 |  | Margham | Area 20 | Train-1/Outdoor Near Vessel-101 | 55.6187245,24.9770004 | Zone 2 | IIB | T3 | Not Available | EE-20-A0-654-01 |  | 20-ITB-15 | 20-ITB-15-1401 | Junction Box | ABTECH | SX.1.5.140 | 219857 | Instrumentation | 2 | Not Available | IEC | Ex e | IIC | T5 | IP66 | Not Available | SIRA | SIRA99ATEX3171 | Not Applicable | Others | Periodic | e | Close | A4. IP washer missing | A4. Install IP washer |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation |  |  | Data Sheet 198 | Ashik Kasim | 2023-06-24 11:39 | A4. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation
199 | 497CA64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.618554,24.9747702 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SFL-201 | 25-PC-492 | Flood Light | EATON | FMVA16LCY-UNV1-76-M20 | Not Available | Electrical | Not Applicable | Not Applicable | NEC | Class 1 Div 2 | ABCD | T4A | Not Available | +55 | UL | Not Available | Not applicable | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 199 | Ashik Kasim | 2023-07-04 09:18 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
200 | 7D5CAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6185682,24.9747058 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-144 | 25-PC-519 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040365 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 200 | Ashik Kasim | 2023-07-04 09:25 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
201 | 445AAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6185452,24.9747512 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-233 | 25-PC-522 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-068 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 201 | Ashik Kasim | 2023-07-04 09:33 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
202 | 3A5FAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6185682,24.9747058 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-129 | 25-PC-493 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040365 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 202 | Ashik Kasim | 2023-07-04 09:43 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
203 | 555DAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6185272,24.9747752 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-231 | 25-PC-550 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | Not visible | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 203 | Ashik Kasim | 2023-07-04 09:47 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
204 | 5A5DAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.618536,24.9747871 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-158 | 25-PC-565 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040354 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 204 | Ashik Kasim | 2023-07-04 09:50 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
205 | B595A64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6184793,24.9747664 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-230 | 25-PC-516 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-020 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 205 | Ashik Kasim | 2023-07-04 10:01 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
206 | 8F5CAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6185301,24.9748098 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-141 | 25-PC-516 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040217 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 206 | Ashik Kasim | 2023-07-04 10:04 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
207 | D45BAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6185288,24.9748876 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SFL-202 | 25-PC-520 | Flood Light | EATON | FMVA16LCY-UNV1-76-M20 | Not Available | Electrical | Not Applicable | Not Applicable | NEC | Class 1 Div 2 | ABCD | T4A | Not Available | +55 | UL | Not Available | Not applicable | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 207 | Ashik Kasim | 2023-07-04 10:20 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
208 | 6E60AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6185551,24.9748381 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-143 | 25-PC-520 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040218 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 208 | Ashik Kasim | 2023-07-04 10:23 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
209 | 295CAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6183408,24.9749511 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-223 | 25-PC-538 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-021 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 209 | Ashik Kasim | 2023-07-04 10:26 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
210 | 3B60AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6183173,24.9749339 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-152 | 25-PC-538 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040337 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 210 | Ashik Kasim | 2023-07-04 10:31 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
211 | 3B60AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6183262,24.9748663 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-243 | 25-PC-504 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-018 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 211 | Ashik Kasim | 2023-07-04 10:37 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
212 | CD5DAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.618323,24.9748762 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-135 | 25-PC-503 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040286 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 212 | Ashik Kasim | 2023-07-04 10:40 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
213 | D559AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6183232,24.9748993 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-242 | 25-PC-558 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-019 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 213 | Ashik Kasim | 2023-07-04 10:44 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
214 | 417DA64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6183431,24.9748185 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-162 | 25-PC-557 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040160 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 214 | Ashik Kasim | 2023-07-04 10:47 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
215 | 735AAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6183366,24.9748198 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-238 | 25-PC-556 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-023 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 215 | Ashik Kasim | 2023-07-04 10:54 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
216 | A795A64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6183504,24.9748238 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-161 | 25-PC-556 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040339 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 216 | Ashik Kasim | 2023-07-04 10:56 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
217 | 9A7DA64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6183366,24.9748198 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-237 | 25-PC-498 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | Not visible | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 217 | Ashik Kasim | 2023-07-04 11:00 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
218 | 2294A64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6183263,24.9747496 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-132 | 25-PC-491 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040334 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 218 | Ashik Kasim | 2023-07-04 11:08 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
219 | 625DAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6184131,24.9750431 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-249 | 25-PC-806 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-123 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 219 | Ashik Kasim | 2023-07-04 15:27 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
220 | EA5BAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6186119,24.9748561 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-265 | 25-PC-806 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040309 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 220 | Ashik Kasim | 2023-07-04 15:30 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
221 | 4757AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6185983,24.9747892 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-166 | 25-PC-566 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040086 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 221 | Ashik Kasim | 2023-07-04 15:35 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
222 | D95FAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6185573,24.9749074 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-232 | 25-PC-566 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-014 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 222 | Ashik Kasim | 2023-07-04 15:49 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
223 | 085CAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (Stairways) | 55.6184324,24.9747479 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-235-A | 25-PC-736 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040102 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 223 | Ashik Kasim | 2023-07-04 15:58 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
224 | 9F5FAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (Stairways) | 55.6184619,24.9747667 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-345 | 25-PC-736 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-091 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 224 | Ashik Kasim | 2023-07-04 16:01 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
225 | E25CAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6184458,24.9746908 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-159 | 25-PC-551 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040328 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 225 | Ashik Kasim | 2023-07-05 08:17 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
226 | 5E62AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6184746,24.9747273 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-234 | 25-PC-552 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-099 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 226 | Ashik Kasim | 2023-07-05 08:24 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
227 | 0F92A64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6184902,24.9747292 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-145 | 25-PC-524 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040287 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 227 | Ashik Kasim | 2023-07-05 08:28 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
228 | CB5DAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6184614,24.9747451 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-235 | 25-PC-524 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-083 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 228 | Ashik Kasim | 2023-07-05 08:32 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
229 | F85AAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.618465,24.9747526 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-160 | 25-PC-554 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040082 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 229 | Ashik Kasim | 2023-07-05 08:38 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
230 | 085FAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6184162,24.9747136 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-236 | 25-PC-554 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-084 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 230 | Ashik Kasim | 2023-07-05 08:46 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
231 | BA57AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.618465,24.9747526 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-142 | 25-PC-517 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040079 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 231 | Ashik Kasim | 2023-07-05 08:49 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
232 | C65DAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6184325,24.9748323 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-239 | 25-PC-518 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-016 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 232 | Ashik Kasim | 2023-07-05 08:56 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
233 | 835CAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6183705,24.9748177 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-165 | 25-PC-564 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040085 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 233 | Ashik Kasim | 2023-07-05 09:01 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
234 | DC5AAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6184332,24.9748376 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-240 | 25-PC-564 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-012 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 234 | Ashik Kasim | 2023-07-05 09:06 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
235 | E15CAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6184557,24.9748231 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-140 | 25-PC-514 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040331 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 235 | Ashik Kasim | 2023-07-05 09:12 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
236 | 6C5DAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.618498,24.9748301 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-241 | 25-PC-514 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-013 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 236 | Ashik Kasim | 2023-07-05 09:18 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
237 | D258AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6185484,24.9748781 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-156 | 25-PC-549 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040333 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 237 | Ashik Kasim | 2023-07-05 09:23 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
238 | 5D5AAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.618498,24.9748301 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-229 | 25-PC-546 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | Not visible | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 238 | Ashik Kasim | 2023-07-05 09:51 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
239 | 645CAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6185513,24.9748956 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-157 | 25-PC-548 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040376 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 239 | Ashik Kasim | 2023-07-05 09:55 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
240 | 5D5DAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6185255,24.9748849 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SFL-203 | 25-PC-548 | Flood Light | EATON | FMVA16LCY-UNV1-76-M20 | Not Available | Electrical | Not Applicable | Not Applicable | NEC | Class 1 Div 2 | ABCD | T4A | Not Available | +55 | UL | Not Available | Not applicable | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 240 | Ashik Kasim | 2023-07-05 10:00 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
241 | 965BAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6185331,24.974901 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-138 | 25-PC-515 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040340 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 241 | Ashik Kasim | 2023-07-05 10:03 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
242 | 455EAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6185738,24.9748977 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-228 | 25-PC-510 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-008 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 242 | Ashik Kasim | 2023-07-05 10:07 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
243 | 245CAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6185463,24.9749349 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-154 | 25-PC-542 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040401 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 243 | Ashik Kasim | 2023-07-05 10:10 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
244 | 885CAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6185492,24.9749281 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-227 | 25-PC-542 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-002 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 244 | Ashik Kasim | 2023-07-05 10:14 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
245 | 245EAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.618582,24.9749465 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-139 | 25-PC-509 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040361 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 245 | Ashik Kasim | 2023-07-05 10:17 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
246 | 8C5CAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6185477,24.9749723 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SFL-204 | 25-PC-512 | Flood Light | EATON | FMVA16LCY-UNV1-76-M20 | Not Available | Electrical | Not Applicable | Not Applicable | NEC | Class 1 Div 2 | ABCD | T4A | Not Available | +55 | UL | Not Available | Not applicable | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 246 | Ashik Kasim | 2023-07-05 10:23 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
247 | FE63AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6185183,24.9749119 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-137 | 25-PC-508 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040285 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 247 | Ashik Kasim | 2023-07-05 15:52 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
248 | D65BAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6184601,24.9749753 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-153 | 25-PC-540 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040336 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 248 | Ashik Kasim | 2023-07-05 15:54 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
249 | 0F5CAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.618371,24.9749529 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-136 | 25-PC-506 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040284 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 249 | Ashik Kasim | 2023-07-05 15:57 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
250 | D15CAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6184281,24.9749891 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-224 | 25-PC-506 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-009 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 250 | Ashik Kasim | 2023-07-05 16:03 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
251 | 107DA64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6184281,24.9749891 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-225 | 25-PC-540 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-007 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 251 | Ashik Kasim | 2023-07-05 16:07 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
252 | 3559AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+30)Top | 55.6184281,24.9749891 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-226 | 25-PC-508 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | Not visible | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 252 | Ashik Kasim | 2023-07-05 16:13 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
253 | 3B5BAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler(Stairways) | 55.618371,24.9749529 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-235-B | 25-PC-703-A | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040277 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 253 | Ashik Kasim | 2023-07-06 06:10 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
254 | AD95A64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler(Stairways) | 55.6183108,24.9746756 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SFL-307 | 25-PC-703-C | Flood Light | EATON | FMVA16LCY-UNV1-76-M20 | Not Available | Electrical | Not Applicable | Not Applicable | NEC | Class 1 Div 2 | ABCD | T4A | Not Available | +55 | UL | Not Available | Not applicable | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 254 | Ashik Kasim | 2023-07-06 06:15 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
255 | 1E7DA64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6183469,24.9747276 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-235 | 25-PC-703 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040276 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 255 | Ashik Kasim | 2023-07-06 06:18 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
256 | 8A93A64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6184281,24.9749891 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-344 | 25-PC-704 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-085 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 256 | Ashik Kasim | 2023-07-06 06:23 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
257 | 0C93A64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6183684,24.9747303 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-130 | 25-PC-497 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040278 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 257 | Ashik Kasim | 2023-07-06 06:27 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
258 | 7457AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.618362,24.9747125 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-217 | 25-PC-494 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-090 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 258 | Ashik Kasim | 2023-07-06 06:34 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
259 | F07EA64E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6183169,24.9747621 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-148 | 25-PC-530 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040374 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 259 | Ashik Kasim | 2023-07-06 06:44 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
260 | 905DAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6182856,24.9747393 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-149 | 25-PC-533 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040271 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 260 | Ashik Kasim | 2023-07-06 08:03 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
261 | BA5CAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.618334,24.9747531 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-218 | 25-PC-532 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-093 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 261 | Ashik Kasim | 2023-07-06 08:08 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
262 | B55BAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6183397,24.9747547 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-131 | 25-PC-499-A | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040181 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 262 | Ashik Kasim | 2023-07-06 08:15 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
263 | 4858AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6183712,24.9748191 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-219 | 25-PC-496 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-088 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 263 | Ashik Kasim | 2023-07-06 08:20 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
264 | 755AAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6184178,24.9748968 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-150 | 25-PC-533 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040172 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 264 | Ashik Kasim | 2023-07-06 08:24 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
265 | 9A5AAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6183157,24.974936 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-221 | 25-PC-534 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-087 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 265 | Ashik Kasim | 2023-07-06 08:28 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
266 | C65CAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6183521,24.9749281 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-134 | 25-PC-501 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040078 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 266 | Ashik Kasim | 2023-07-06 08:44 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
267 | ED5BAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6182879,24.9749486 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-222 | 25-PC-534 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-092 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 267 | Ashik Kasim | 2023-07-06 08:52 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
268 | 6059AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6183155,24.9748201 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-133 | 25-PC-499 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040134 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 268 | Ashik Kasim | 2023-07-06 09:00 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
269 | 2F5BAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6183398,24.9748506 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-220 | 25-PC-500 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-089 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 269 | Ashik Kasim | 2023-07-06 09:06 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
270 | C25DAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183215,24.974609 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-202 | 25-PC-638 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040094 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 270 | Ashik Kasim | 2023-07-06 09:13 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
271 | 7B58AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183306,24.9746095 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-322 | 25-PC-638 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-101 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 271 | Ashik Kasim | 2023-07-06 09:20 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
272 | 825CAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183889,24.9745673 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-201 | 25-PC-635-A | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040238 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 272 | Ashik Kasim | 2023-07-06 09:24 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
273 | B35DAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183784,24.9745613 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-320 | 25-PC-636 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-097 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 273 | Ashik Kasim | 2023-07-06 09:28 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
274 | 125CAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183699,24.974498 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-218 | 25-PC-669 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040267 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 274 | Ashik Kasim | 2023-07-06 09:34 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
275 | B35CAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183703,24.9744877 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-318 | 25-PC-670 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-103 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 275 | Ashik Kasim | 2023-07-06 09:40 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
276 | 5058AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183566,24.9744544 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-199 | 25-PC-633 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040186 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 276 | Ashik Kasim | 2023-07-06 09:45 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
277 | DA5BAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183703,24.9744877 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-317 | 25-PC-632 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-096 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 277 | Ashik Kasim | 2023-07-06 09:49 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
278 | 6F57AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6182684,24.9745611 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-200 | 25-PC-634 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040149 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 278 | Ashik Kasim | 2023-07-06 09:54 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
279 | C25CAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183282,24.9744837 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-319 | 25-PC-634 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-098 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 279 | Ashik Kasim | 2023-07-06 10:02 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
280 | 4D58AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183344,24.9746414 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-219 | 25-PC-671 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040127 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 280 | Ashik Kasim | 2023-07-06 10:06 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
281 | BB63AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6182254,24.9745955 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-321 | 25-PC-672 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-102 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 281 | Ashik Kasim | 2023-07-06 10:11 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
282 | 4057AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6186034,24.9744428 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SFL-303 | 25-PC-686 | Flood Light | EATON | FMVA16LCY-UNV1-76-M20 | Not Available | Electrical | 2 | Not Available | IEC | Ex ec mb | IIC | T4 | IP66 | -40 +55 | DEMKO | DEMKO 15 ATEX 1383/1377X | Yes | Lighting | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 282 | Ashik Kasim | 2023-07-07 05:50 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
283 | D25BAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6185526,24.9744617 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-226 | 25-PC-687 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040123 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 283 | Ashik Kasim | 2023-07-07 05:53 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
284 | 2D5BAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6185548,24.9744529 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-333 | 25-PC-656 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-119 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 284 | Ashik Kasim | 2023-07-07 05:58 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
285 | C95CAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6185633,24.9744309 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-211 | 25-PC-653 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040373 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 285 | Ashik Kasim | 2023-07-07 06:04 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
286 | 9B5BAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6185548,24.9744529 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-331 | 25-PC-688 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-120 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 286 | Ashik Kasim | 2023-07-07 06:12 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
287 | BC57AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6185466,24.9744662 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-227 | 25-PC-685 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040353 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 287 | Ashik Kasim | 2023-07-07 06:11 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
288 | 345BAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6185698,24.9745124 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-330 | 25-PC-652 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-105 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 288 | Ashik Kasim | 2023-07-07 06:17 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
289 | D059AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6185686,24.9745092 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-209 | 25-PC-652 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040126 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 289 | Ashik Kasim | 2023-07-07 06:20 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
290 | 585CAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6185708,24.9745005 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SFL-304 | 25-PC-650 | Flood Light | EATON | FMVA16LCY-UNV1-76-M20 | Not Available | Electrical | 2 | Not Available | IEC | Ex ec mb | IIC | T4 | IP66 | -40 +55 | DEMKO | DEMKO 15 ATEX 1383/1377X | Yes | Lighting | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 290 | Ashik Kasim | 2023-07-07 06:22 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
291 | BD5DAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6185361,24.9745163 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-208 | 25-PC-659 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040344 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 291 | Ashik Kasim | 2023-07-07 06:26 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
292 | 225CAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.618551,24.9745523 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-329 | 25-PC-684 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-114 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 292 | Ashik Kasim | 2023-07-07 06:32 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
293 | D65AAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6185892,24.9745412 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-225 | 25-PC-684 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040177 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 293 | Ashik Kasim | 2023-07-07 06:35 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
294 | 415EAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6185532,24.9745725 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SFL-305 | 25-PC-682 | Flood Light | EATON | FMVA16LCY-UNV1-76-M20 | Not Available | Electrical | 2 | Not Available | IEC | Ex ec mb | IIC | T4 | IP66 | -40 +55 | DEMKO | DEMKO 15 ATEX 1383/1377X | Yes | Lighting | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 294 | Ashik Kasim | 2023-07-07 06:38 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
295 | 435BAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6185382,24.9745897 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-224 | 25-PC-699 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040352 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 295 | Ashik Kasim | 2023-07-07 06:41 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
296 | 5E5BAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6185164,24.9745815 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-207 | 25-PC-647 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040282 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 296 | Ashik Kasim | 2023-07-07 08:21 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
297 | AC5CAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6185783,24.9745573 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-328 | 25-PC-648 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-112 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 297 | Ashik Kasim | 2023-07-07 08:28 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
298 | 0E5BAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6185522,24.9746075 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-223 | 25-PC-681 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040167 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 298 | Ashik Kasim | 2023-07-07 08:31 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
299 | B15BAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6185783,24.9745573 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-327 | 25-PC-680 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-110 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 299 | Ashik Kasim | 2023-07-07 08:37 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
300 | 555AAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6185441,24.9746577 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SFL-306 | 25-PC-630 | Flood Light | EATON | FMVA16LCY-UNV1-76-M20 | Not Available | Electrical | 2 | Not Available | IEC | Ex ec mb | IIC | T4 | IP66 | -40 +55 | DEMKO | DEMKO 15 ATEX 1383/1377X | Yes | Lighting | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 300 | Ashik Kasim | 2023-07-07 08:40 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
301 | 8557AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6185522,24.9746075 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-223-A | 25-PC-681-A | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040358 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 301 | Ashik Kasim | 2023-07-07 08:45 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
302 | A65BAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6185522,24.9746075 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-206 | 25-PC-647 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040300 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 302 | Ashik Kasim | 2023-07-07 08:50 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
303 | 985DAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6185,24.9746485 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-326 | 25-PC-646 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-308 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 303 | Ashik Kasim | 2023-07-07 08:55 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
304 | 495CAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.618449,24.9746474 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-222 | 25-PC-678 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040131 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 304 | Ashik Kasim | 2023-07-07 08:58 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
305 | 0A5AAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6184365,24.9746343 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-325 | 25-PC-678 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-305 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 305 | Ashik Kasim | 2023-07-07 09:03 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
306 | A559AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.618449,24.9746474 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-205 | 25-PC-678 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040297 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 306 | Ashik Kasim | 2023-07-07 09:07 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
307 | 1E5BAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6183961,24.9746633 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-324 | 25-PC-644 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-306 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 307 | Ashik Kasim | 2023-07-07 09:15 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
308 | 3E59AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6183437,24.9746369 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-323 | 25-PC-676 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | Not Visible | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 308 | Ashik Kasim | 2023-07-07 09:19 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
309 | 4257AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6183396,24.9746552 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-221 | 25-PC-677 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040135 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 309 | Ashik Kasim | 2023-07-07 09:22 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
310 | 4857AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6183465,24.974567 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-204 | 25-PC-641 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040295 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 310 | Ashik Kasim | 2023-07-07 09:26 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
311 | C55AAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6183377,24.9745708 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-343 | 25-PC-642 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-115 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 311 | Ashik Kasim | 2023-07-07 09:32 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
312 | AA5AAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6183575,24.9745379 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-231 | 25-PC-693 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040170 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 312 | Ashik Kasim | 2023-07-07 09:36 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
313 | 7E5DAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6183377,24.9745708 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-342 | 25-PC-696 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-121 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 313 | Ashik Kasim | 2023-07-07 09:38 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
314 | 7062AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.61836,24.9745449 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-230 | 25-PC-675 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040130 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 314 | Ashik Kasim | 2023-07-07 09:44 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
315 | CC5CAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.618342,24.974483 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-338 | 25-PC-694 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-123 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 315 | Ashik Kasim | 2023-07-07 09:48 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
316 | 865AAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6183547,24.9744912 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-203 | 25-PC-640 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040293 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 316 | Ashik Kasim | 2023-07-07 09:59 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
317 | DC58AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6183283,24.9744836 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-337 | 25-PC-640 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-121 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 317 | Ashik Kasim | 2023-07-07 10:04 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
318 | FA5AAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6185302,24.9744625 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-210 | 25-PC-654 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040264 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 318 | Ashik Kasim | 2023-07-10 05:40 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
319 | 035AAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6185387,24.974456 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SFL-302 | 25-PC-654 | Flood Light | EATON | FMVA16LCY-UNV1-76-M20 | Not Available | Electrical | 2 | Not Available | IEC | Ex ec mb | IIC | T4 | IP66 | -40 +55 | DEMKO | DEMKO 15 ATEX 1383/1377X | Yes | Lighting | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 319 | Ashik Kasim | 2023-07-10 05:42 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
320 | 0E5CAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.61854,24.9744706 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-228 | 25-PC-690 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040263 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 320 | Ashik Kasim | 2023-07-10 05:46 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
321 | B664AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6185312,24.9744692 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-334 | 25-PC-690 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | Not visible | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 321 | Ashik Kasim | 2023-07-10 05:52 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
322 | 6A5CAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6184919,24.9744789 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-212 | 25-PC-631 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040296 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 322 | Ashik Kasim | 2023-07-10 05:57 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
323 | 085BAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6184775,24.9744712 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-335 | 25-PC-658 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-117 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 323 | Ashik Kasim | 2023-07-10 06:00 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
324 | B45BAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6184919,24.9744789 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-198 | 25-PC-733 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040296 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 324 | Ashik Kasim | 2023-07-10 06:05 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
325 | 485EAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6184414,24.9744597 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SFL-301 | 25-PC-633 | Flood Light | EATON | FMVA16LCY-UNV1-76-M20 | Not Available | Electrical | 2 | Not Available | IEC | Ex ec mb | IIC | T4 | IP66 | -40 +55 | DEMKO | DEMKO 15 ATEX 1383/1377X | Yes | Lighting | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 325 | Ashik Kasim | 2023-07-10 06:07 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
326 | 2E5EAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6184624,24.9744468 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-229 | 25-PC-691 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040098 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 326 | Ashik Kasim | 2023-07-10 06:10 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
327 | DD5AAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6184321,24.9744442 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-336 | 25-PC-692 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-116 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 327 | Ashik Kasim | 2023-07-10 06:20 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
328 | 5458AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6184147,24.9745107 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-214 | 25-PC-662 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040096 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 328 | Ashik Kasim | 2023-07-10 06:24 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
329 | 9D5AAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6184436,24.9745275 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-339 | 25-PC-662 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-124 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 329 | Ashik Kasim | 2023-07-10 06:26 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
330 | 3C60AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6184887,24.9745309 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-233 | 25-PC-669 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040100 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 330 | Ashik Kasim | 2023-07-10 06:31 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
331 | 385CAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6184436,24.9745275 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-340 | 25-PC-700 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-109 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 331 | Ashik Kasim | 2023-07-10 06:33 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
332 | 9F60AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6185313,24.9745116 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-213 | 25-PC-659 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040262 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 332 | Ashik Kasim | 2023-07-10 06:35 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
333 | 6A63AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6185959,24.9745156 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-341 | 25-PC-660 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-108 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 333 | Ashik Kasim | 2023-07-10 06:43 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
334 | 8358AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6184244,24.9743503 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-274 | 25-PC-803 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040317 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 334 | Ashik Kasim | 2023-07-10 08:22 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
335 | E15AAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6183887,24.9744318 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-346 | 25-PC-824 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-079 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 335 | Ashik Kasim | 2023-07-10 08:26 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
336 | B957AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6186244,24.9744947 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-285 | 25-PC-845 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040105 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 336 | Ashik Kasim | 2023-07-10 08:33 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
337 | 725EAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.61843,24.9744273 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-357 | 25-PC-846 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-095 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 337 | Ashik Kasim | 2023-07-10 08:36 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
338 | 3264AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6184796,24.9744539 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-275 | 25-PC-827 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040318 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 338 | Ashik Kasim | 2023-07-10 08:45 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
339 | 135BAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6184332,24.974378 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-347 | 25-PC-826 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-069 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 339 | Ashik Kasim | 2023-07-10 08:48 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
340 | 3C5EAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6184978,24.9744943 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-276 | 25-PC-829 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040319 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 340 | Ashik Kasim | 2023-07-10 08:54 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
341 | A55BAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.618598,24.9744925 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-348 | 25-PC-828 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-024 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 341 | Ashik Kasim | 2023-07-10 08:57 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
342 | 8957AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6186044,24.9744888 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-234 | 25-PC-701 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040101 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 342 | Ashik Kasim | 2023-07-10 09:00 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
343 | 4C5AAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6186538,24.9744871 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-332 | 25-PC-702 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-001 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 343 | Ashik Kasim | 2023-07-10 09:07 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
344 | 305BAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6186367,24.9744681 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-279 | 25-PC-833 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040322 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 344 | Ashik Kasim | 2023-07-10 09:00 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
345 | 2C5BAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6185443,24.9746025 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-351 | 25-PC-834 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-001 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 345 | Ashik Kasim | 2023-07-10 09:21 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
346 | 2058AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6185908,24.9745017 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-284 | 25-PC-843 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040327 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 346 | Ashik Kasim | 2023-07-10 09:28 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
347 | FC5BAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6185852,24.9744986 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-356 | 25-PC-844 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-075 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 347 | Ashik Kasim | 2023-07-10 09:31 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
348 | 605BAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.618296,24.9745556 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-278 | 25-PC-833 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040321 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 348 | Ashik Kasim | 2023-07-10 09:50 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
349 | 1C5BAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6185852,24.9744986 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-350 | 25-PC-832 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-080 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 349 | Ashik Kasim | 2023-07-10 09:52 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
350 | 0C5EAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6183876,24.9745696 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-277 | 25-PC-829 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040320 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 350 | Ashik Kasim | 2023-07-10 09:57 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
351 | 6B63AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6183456,24.9745593 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-349 | 25-PC-830 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-074 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 351 | Ashik Kasim | 2023-07-10 10:05 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
352 | E35AAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6184726,24.9747093 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-283 | 25-PC-841 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040326 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 352 | Ashik Kasim | 2023-07-11 05:42 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
353 | 8657AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6185063,24.9746955 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-355 | 25-PC-842 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-070 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 353 | Ashik Kasim | 2023-07-11 05:45 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
354 | D45AAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6184905,24.9746672 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-282 | 25-PC-839 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040325 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 354 | Ashik Kasim | 2023-07-11 05:48 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
355 | 195CAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6184104,24.9747855 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-354 | 25-PC-840 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-065 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 355 | Ashik Kasim | 2023-07-11 05:54 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
356 | 4059AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6184079,24.9747188 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-280 | 25-PC-835 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040323 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 356 | Ashik Kasim | 2023-07-11 05:57 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
357 | C262AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6185384,24.9746582 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-352 | 25-PC-836 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-076 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 357 | Ashik Kasim | 2023-07-11 05:58 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
358 | 1958AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6184428,24.9746786 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-281 | 25-PC-837 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040201 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 358 | Ashik Kasim | 2023-07-11 06:02 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
359 | B458AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6184231,24.9746989 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-353 | 25-PC-838 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-071 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 359 | Ashik Kasim | 2023-07-11 06:07 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
360 | 6C5FAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6184913,24.9744916 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-303 | 25-PC-664 | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-007 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 360 | Ashik Kasim | 2023-07-11 06:21 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
361 | 205EAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6186728,24.9743887 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-215 | 25-PC-663 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040151 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 361 | Ashik Kasim | 2023-07-11 06:29 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
362 | CE59AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6184993,24.9742025 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-306 | 25-PC-698 | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-006 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 362 | Ashik Kasim | 2023-07-11 06:33 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
363 | D95AAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6185317,24.9747264 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-232 | 25-PC-697 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040099 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 363 | Ashik Kasim | 2023-07-11 06:36 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
364 | 295EAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6184993,24.9742025 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-304 | 25-PC-666 | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-004 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 364 | Ashik Kasim | 2023-07-11 07:56 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
365 | FF5DAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6183115,24.974547 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-216 | 25-PC-665 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040097 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 365 | Ashik Kasim | 2023-07-11 08:02 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
366 | E95AAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6182848,24.9744209 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-303 | 25-PC-668 | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-005 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 366 | Ashik Kasim | 2023-07-11 08:08 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
367 | 845DAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6182894,24.9744234 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-217 | 25-PC-667 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040373 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 367 | Ashik Kasim | 2023-07-11 08:15 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
368 | 925DAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.618274,24.9745684 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-302 | 25-PC-635 | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-003 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 368 | Ashik Kasim | 2023-07-11 08:21 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
369 | F45AAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6182722,24.974516 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-200-A | 25-PC-667 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040251 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 369 | Ashik Kasim | 2023-07-11 08:23 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
370 | A55EAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6185544,24.9746888 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-301 | 25-PC-674 | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-002 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 370 | Ashik Kasim | 2023-07-11 08:35 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
371 | 7157AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6183118,24.9746484 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-220 | 25-PC-703 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040347 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 371 | Ashik Kasim | 2023-07-11 08:43 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
372 | 8857AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6183166,24.9746627 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-203 | 25-PC-530 | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-014 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close | B6. Broken earth connection | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable | 1, Earth Cable Meters 1 | Data Sheet 372 | Ashik Kasim | 2023-07-11 10:43 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-25 06:41
373 | 8F5DAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6184969,24.9745572 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-205 | 25-PC-526 | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-012 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close | B6. Broken earth connection | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable | 1, Earth Cable Meters 1 | Data Sheet 373 | Ashik Kasim | 2023-07-11 10:40 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-25 05:59
374 | 435CAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6185124,24.9749531 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-146 | 25-PC-525 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040183 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 374 | Ashik Kasim | 2023-07-11 09:20 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
375 | 015EAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6185749,24.9748748 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-206 | 25-PC-561 | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-009 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close | B6. Broken earth connection | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable | 1, Earth Cable Meters 1 | Data Sheet 375 | Ashik Kasim | 2023-07-11 10:34 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-25 06:29
376 | 1357AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6185175,24.9749525 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-164 | 25-PC-562 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040084 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 376 | Ashik Kasim | 2023-07-11 09:35 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
377 | B25AAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6184318,24.9749383 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-204 | 25-PC-528 | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-011 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 377 | Ashik Kasim | 2023-07-11 09:43 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
378 | 6C59AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6183009,24.9748678 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-147 | 25-PC-527 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040081 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 378 | Ashik Kasim | 2023-07-11 09:50 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
379 | 645AAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6183292,24.9748528 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-202 | 25-PC-499-B | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-016 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 379 | Ashik Kasim | 2023-07-11 09:56 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
380 | 605DAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.618338,24.9748738 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-131-A | 25-PC-499-B | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040211 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 380 | Ashik Kasim | 2023-07-11 10:00 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
381 | 7957AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6181553,24.9750063 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-201 | 25-PC-536 | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-010 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 381 | Ashik Kasim | 2023-07-11 10:19 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
382 | DD5DAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.618316,24.9749819 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-151 | 25-PC-535 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040236 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 382 | Ashik Kasim | 2023-07-11 10:31 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
383 | B858AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6182992,24.9745458 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SOC-926 | 25-PC-926 | Power Socket-220v/250v | Marechal Electric France | DXA1 2914015 | Not Available | Electrical | 2 | Gb | IEC | Ex de | IIC | T5 | IP66/67 | -55 +60 | LCIE | LCIE15ATEX3033X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 383 | Ashik Kasim | 2023-07-11 10:55 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
384 | B25CAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6183267,24.974797 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SOC-201B | 25-PC-923 | Power Socket-220v/250v | Marechal Electric France | DXA1 2914015 | Not Available | Electrical | 2 | Gb | IEC | Ex de | IIC | T5 | IP66/67 | -55 +60 | LCIE | LCIE15ATEX3033X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 384 | Ashik Kasim | 2023-07-11 11:00 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
385 | 095FAB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6184448,24.9750937 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SOC-101B | 25-PC-919 | Power Socket-220v/250v | Marechal Electric France | DXA1 2914015 | Not Available | Electrical | 2 | Gb | IEC | Ex de | IIC | T5 | IP66/67 | -55 +60 | LCIE | LCIE15ATEX3033X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 385 | Ashik Kasim | 2023-07-12 05:37 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
386 | 135EAB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6183569,24.9750482 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-103 | 25-PC-396 | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-038 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 386 | Ashik Kasim | 2023-07-12 05:45 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
387 | 585AAB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6185619,24.975018 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-105 | 25-PC-392 | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-036 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 387 | Ashik Kasim | 2023-07-12 05:48 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
388 | AE58AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6185828,24.9750181 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-079 | 25-PC-391 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040210 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 388 | Ashik Kasim | 2023-07-12 05:51 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
389 | A259AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6185811,24.9751857 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-106 | 25-PC-416 | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-040 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 389 | Ashik Kasim | 2023-07-12 05:58 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
390 | EA5CAB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6184812,24.9752111 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-091 | 25-PC-415 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040068 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 390 | Ashik Kasim | 2023-07-12 06:07 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
391 | A362AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6183531,24.9750939 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-104 | 25-PC-394 | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-033 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close | B6. Broken earth connection | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable | 1, Earth Cable Meters 1 | Data Sheet 391 | Ashik Kasim | 2023-07-12 06:11 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-24 06:19
392 | 1658AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6183187,24.975102 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-080 | 25-PC-393 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040066 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 392 | Ashik Kasim | 2023-07-12 06:13 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
393 | 4E5DAB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6182277,24.9752048 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-102 | 25-PC-373-A | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-044 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 393 | Ashik Kasim | 2023-07-12 06:22 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
394 | 615DAB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6182791,24.9751883 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-069-A | 25-PC-373 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040165 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 394 | Ashik Kasim | 2023-07-12 06:26 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
395 | 5C5DAB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6182237,24.975182 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-101 | 25-PC-404 | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-046 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 395 | Ashik Kasim | 2023-07-12 06:31 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
396 | CB5BAB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6182956,24.9753113 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-085 | 25-PC-403 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040180 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 396 | Ashik Kasim | 2023-07-12 06:35 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
397 | E32DAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6181054,24.9750845 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-020 | 25-PC-273 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040055 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 397 | Ashik Kasim | 2023-07-12 08:12 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
398 | 3132AA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179826,24.9749649 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-108 | 25-PC-274 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-062 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 398 | Ashik Kasim | 2023-07-12 08:19 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
399 | 9E2BAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6181187,24.9751027 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-031 | 25-PC-295 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040058 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 399 | Ashik Kasim | 2023-07-12 08:12 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
400 | F85BAB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6181614,24.9751174 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-109 | 25-PC-296 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-063 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 400 | Ashik Kasim | 2023-07-12 08:27 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
401 | 4830AA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6181199,24.9751071 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-030 | 25-PC-293 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040258 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 401 | Ashik Kasim | 2023-07-12 08:32 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
402 | B82AAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6181077,24.9750949 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-110 | 25-PC-294 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-057 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 402 | Ashik Kasim | 2023-07-12 08:36 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
403 | 6E8BAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6181152,24.9750891 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-029 | 25-PC-291 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040195 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 403 | Ashik Kasim | 2023-07-12 08:44 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
404 | 1A2BAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6180945,24.9751513 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-111 | 25-PC-292 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-056 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 404 | Ashik Kasim | 2023-07-12 08:50 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
405 | B72AAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6180697,24.9751082 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-028 | 25-PC-289 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040222 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 405 | Ashik Kasim | 2023-07-12 08:54 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
406 | 3D2FAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6180714,24.9751225 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-112 | 25-PC-290 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-047 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 406 | Ashik Kasim | 2023-07-12 08:58 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
407 | 152FAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6180819,24.9751045 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-027 | 25-PC-287 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040228 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 407 | Ashik Kasim | 2023-07-12 09:06 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
408 | BE2DAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179779,24.9751578 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-113 | 25-PC-288 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-061 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 408 | Ashik Kasim | 2023-07-12 09:12 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
409 | 9A2BAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179379,24.9751305 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-026 | 25-PC-285 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040346 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 409 | Ashik Kasim | 2023-07-12 09:16 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
410 | E62DAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179457,24.9751495 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-114 | 25-PC-286 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-050 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 410 | Ashik Kasim | 2023-07-12 09:20 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
411 | 335AAB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6178846,24.9750632 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-011 | 25-PC-255 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040348 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 411 | Ashik Kasim | 2023-07-12 09:34 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
412 | CB2CAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179457,24.9751495 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-115 | 25-PC-256 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-048 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 412 | Ashik Kasim | 2023-07-12 09:43 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
413 | F62DAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179066,24.9751265 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-012 | 25-PC-257 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040226 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 413 | Ashik Kasim | 2023-07-12 09:45 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
414 | B22CAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179088,24.9751435 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-116 | 25-PC-258 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-049 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 414 | Ashik Kasim | 2023-07-12 09:48 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
415 | B75AAB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179132,24.9751009 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-013 | 25-PC-259 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040206 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 415 | Ashik Kasim | 2023-07-12 09:52 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
416 | B057AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179441,24.9750788 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-101 | 25-PC-260 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-099 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 416 | Ashik Kasim | 2023-07-12 09:58 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
417 | 702FAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6180108,24.97508 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-014 | 25-PC-262 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040230 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 417 | Ashik Kasim | 2023-07-13 05:35 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
418 | E82DAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179759,24.9750213 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-102 | 25-PC-262 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-054 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 418 | Ashik Kasim | 2023-07-13 05:40 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
419 | 465CAB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6180841,24.975046 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-015 | 25-PC-264 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040242 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 419 | Ashik Kasim | 2023-07-13 05:45 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
420 | AA2EAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.618055,24.9750009 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-103 | 25-PC-264 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-054 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 420 | Ashik Kasim | 2023-07-13 05:52 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
421 | 642DAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6180131,24.9750157 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-016 | 25-PC-267 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040269 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 421 | Ashik Kasim | 2023-07-13 05:54 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
422 | 3C2BAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.618055,24.9750009 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-104 | 25-PC-266 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-046 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 422 | Ashik Kasim | 2023-07-13 06:00 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
423 | CB2DAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6181098,24.9751189 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-017 | 25-PC-269 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040225 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 423 | Ashik Kasim | 2023-07-13 06:04 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
424 | AC2DAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.618194,24.9750591 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-105 | 25-PC-268 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-045 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 424 | Ashik Kasim | 2023-07-13 06:07 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
425 | AE2DAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6181442,24.9750893 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-018 | 25-PC-270 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040233 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 425 | Ashik Kasim | 2023-07-13 06:17 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
426 | B52DAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.618158,24.9750601 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-106 | 25-PC-270 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-051 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 426 | Ashik Kasim | 2023-07-13 06:22 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
427 | A42CAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6181812,24.9750215 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-019 | 25-PC-272 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040232 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 427 | Ashik Kasim | 2023-07-13 06:24 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
428 | D35AAB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6182102,24.9750708 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-107 | 25-PC-272 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-052 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 428 | Ashik Kasim | 2023-07-13 06:38 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
429 | 6AC1AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area | 55.6180645,24.9751626 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SOC-101A | 25-PC-920 | Power Socket-220v/250v | Marechal Electric France | DXA1 2914015 | Not Available | Electrical | 2 | Gb | IEC | Ex de | IIC | T5 | IP66/67 | -55 +60 | LCIE | LCIE15ATEX3033X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 429 | Ashik Kasim | 2023-07-13 08:02 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
430 | 7830AA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area | 55.6180873,24.9751997 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SJB-101 | 25-PC-724 | Power Socket Junction Box | Weidmuller | Klippon POK 252512 Ex | XB-AE-A-008830 | Electrical | 2 | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IBExU13ATEX1004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 430 | Ashik Kasim | 2023-07-13 10:08 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
431 | C0C1AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6181315,24.9747703 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-110 | 25-PC-454 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040072 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 431 | Ashik Kasim | 2023-07-13 08:35 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
432 | C92DAA4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6181259,24.9747243 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-208 | 25-PC-454 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-004 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 432 | Ashik Kasim | 2023-07-13 08:40 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
433 | FD31AA4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6181388,24.9747574 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-122 | 25-PC-478 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040075 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 433 | Ashik Kasim | 2023-07-13 08:47 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
434 | E22EAA4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6182272,24.9748393 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-209 | 25-PC-478 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-011 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 434 | Ashik Kasim | 2023-07-13 08:52 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
435 | 8430AA4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6181534,24.9748783 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-121 | 25-PC-477 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040137 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 435 | Ashik Kasim | 2023-07-13 08:58 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
436 | 292EAA4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6181178,24.9748386 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-210 | 25-PC-476 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-016 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 436 | Ashik Kasim | 2023-07-13 09:04 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
437 | 4C2DAA4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6180437,24.9748747 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-120 | 25-PC-475 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040330 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 437 | Ashik Kasim | 2023-07-13 09:12 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
438 | 192DAA4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6180709,24.9748198 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-211 | 25-PC-474 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-023 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 438 | Ashik Kasim | 2023-07-13 09:16 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
439 | 3F2BAA4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6181177,24.97494 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-119 | 25-PC-471 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040292 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 439 | Ashik Kasim | 2023-07-13 09:19 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
440 | 8B2DAA4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6180694,24.974828 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-212 | 25-PC-472 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-017 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 440 | Ashik Kasim | 2023-07-13 09:23 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
441 | 982AAA4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6179415,24.9749668 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-118 | 25-PC-469 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040304 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 441 | Ashik Kasim | 2023-07-13 09:29 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
442 | 5C2EAA4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6180694,24.974828 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-213 | 25-PC-470 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-012 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 442 | Ashik Kasim | 2023-07-13 09:35 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
443 | 165EAB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6179164,24.9747812 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-117 | 25-PC-467 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040368 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 443 | Ashik Kasim | 2023-07-13 09:39 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
444 | C7C2AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6179718,24.9747897 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-214 | 25-PC-468 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-024 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 444 | Ashik Kasim | 2023-07-13 09:42 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
445 | 685DAB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6178904,24.974765 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-101 | 25-PC-433 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040357 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 445 | Ashik Kasim | 2023-07-13 09:48 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
446 | 052DAA4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6178556,24.974757 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-215 | 25-PC-434 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-022 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 446 | Ashik Kasim | 2023-07-13 09:54 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
447 | D52CAA4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area | 55.6180645,24.9751626 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SOC-201A | 25-PC-922 | Power Socket-220v/250v | Marechal Electric France | DXA1 2914015 | Not Available | Electrical | 2 | Gb | IEC | Ex de | IIC | T5 | IP66/67 | -55 +60 | LCIE | LCIE15ATEX3033X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 447 | Ashik Kasim | 2023-07-13 10:01 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
448 | BB2BAA4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area | 55.6180873,24.9751997 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SJB-201 | 25-PC-726 | Power Socket Junction Box | Weidmuller | Klippon POK 252512 Ex | XB-AE-A-008830 | Electrical | 2 | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IBExU13ATEX1004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 448 | Ashik Kasim | 2023-07-13 12:58 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
449 | C22AAA4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6179064,24.9747848 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-102 | 25-PC-435 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040188 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 449 | Ashik Kasim | 2023-07-14 05:36 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
450 | 0A5CAB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6178907,24.9748208 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-216 | 25-PC-436 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-013 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 450 | Ashik Kasim | 2023-07-14 05:42 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
451 | 335BAB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6179418,24.9747385 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-103 | 25-PC-439 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040189 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 451 | Ashik Kasim | 2023-07-14 05:51 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
452 | 202EAA4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6178907,24.9748208 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-201 | 25-PC-440 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-020 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 452 | Ashik Kasim | 2023-07-14 05:56 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
453 | 465DAB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6179169,24.9747581 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-104 | 25-PC-443 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040190 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 453 | Ashik Kasim | 2023-07-14 05:58 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
454 | 7F30AA4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.617971,24.97472 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-202 | 25-PC-442 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-116 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 454 | Ashik Kasim | 2023-07-14 06:04 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
455 | 22C1AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6180562,24.9747888 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-105 | 25-PC-445 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040191 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 455 | Ashik Kasim | 2023-07-14 06:07 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
456 | 492CAA4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6179877,24.9746401 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-203 | 25-PC-444 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-116 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 456 | Ashik Kasim | 2023-07-14 06:12 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
457 | E730AA4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6180602,24.9747435 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-106 | 25-PC-445 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040192 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 457 | Ashik Kasim | 2023-07-14 06:18 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
458 | 905BAB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6180317,24.9747053 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-204 | 25-PC-446 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-003 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 458 | Ashik Kasim | 2023-07-14 06:21 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
459 | ACC5AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6181037,24.9747244 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-107 | 25-PC-447 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040193 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 459 | Ashik Kasim | 2023-07-14 06:25 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
460 | BE2BAA4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6181184,24.9747337 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-205 | 25-PC-448 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-021 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 460 | Ashik Kasim | 2023-07-14 06:30 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
461 | D65EAB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6181516,24.9747769 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-108 | 25-PC-449 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040194 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 461 | Ashik Kasim | 2023-07-14 06:31 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
462 | 6B5CAB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6181716,24.9747149 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-206 | 25-PC-450 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-010 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 462 | Ashik Kasim | 2023-07-14 06:34 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
463 | 665CAB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.618184,24.9747647 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-109 | 25-PC-451 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040136 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 463 | Ashik Kasim | 2023-07-14 08:22 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
464 | 7357AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6182444,24.974767 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-207 | 25-PC-452 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-005 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 464 | Ashik Kasim | 2023-07-14 08:26 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
465 | 1A2CAA4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6181888,24.9744685 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-178 | 25-PC-451 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040087 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 465 | Ashik Kasim | 2023-07-14 08:38 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
466 | 8CBFAB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6181769,24.9744539 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-308 | 25-PC-590 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-094 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 466 | Ashik Kasim | 2023-07-14 08:42 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
467 | 8F2BAA4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6181811,24.9744971 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-191 | 25-PC-615 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040091 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 467 | Ashik Kasim | 2023-07-14 08:45 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
468 | C0BFAB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6181409,24.974572 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-309 | 25-PC-616 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-107 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 468 | Ashik Kasim | 2023-07-14 08:50 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
469 | F12AAA4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6181271,24.9745288 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-190 | 25-PC-613 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040299 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 469 | Ashik Kasim | 2023-07-14 08:54 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
470 | 0A2FAA4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6181586,24.9745303 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-310 | 25-PC-614 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-912 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 470 | Ashik Kasim | 2023-07-14 09:01 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
471 | 022EAA4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6181492,24.9745214 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-189 | 25-PC-611 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040182 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 471 | Ashik Kasim | 2023-07-14 09:04 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
472 | 6A2CAA4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6181209,24.9745394 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-311 | 25-PC-612 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-109 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 472 | Ashik Kasim | 2023-07-14 09:08 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
473 | 2F2BAA4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.618117,24.9744953 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-188 | 25-PC-609 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040125 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 473 | Ashik Kasim | 2023-07-14 09:11 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
474 | EA30AA4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6180987,24.9745468 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-312 | 25-PC-610 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-108 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 474 | Ashik Kasim | 2023-07-14 09:14 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
475 | C92BAA4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179509,24.9745519 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-187 | 25-PC-607 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040140 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 475 | Ashik Kasim | 2023-07-14 09:21 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
476 | B330AA4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179764,24.9745597 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-313 | 25-PC-608 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-066 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 476 | Ashik Kasim | 2023-07-14 09:28 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
477 | 422FAA4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6182233,24.9744572 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-177 | 25-PC-588 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040169 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 477 | Ashik Kasim | 2023-07-14 09:43 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
478 | D42AAA4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6182068,24.9744348 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-307 | 25-PC-588 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-001 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 478 | Ashik Kasim | 2023-07-14 09:48 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
479 | 192CAA4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.618139,24.9744335 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-176 | 25-PC-585 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040265 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 479 | Ashik Kasim | 2023-07-14 09:51 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
480 | 712BAA4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.618158,24.9744466 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-306 | 25-PC-586 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-002 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 480 | Ashik Kasim | 2023-07-14 09:58 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
481 | 0B2DAA4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6180984,24.9744344 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-175 | 25-PC-583 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040120 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 481 | Ashik Kasim | 2023-07-17 05:40 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
482 | DA2EAA4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6181238,24.9744504 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-305 | 25-PC-584 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-019 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 482 | Ashik Kasim | 2023-07-17 05:46 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
483 | 912BAA4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6180984,24.9744344 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-174 | 25-PC-581 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040128 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 483 | Ashik Kasim | 2023-07-17 05:49 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
484 | D72AAA4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6180496,24.9744724 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-173 | 25-PC-579 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040158 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 484 | Ashik Kasim | 2023-07-17 05:51 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
485 | B42AAA4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6180599,24.9744527 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-304 | 25-PC-580 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-100 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 485 | Ashik Kasim | 2023-07-17 05:56 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
486 | F4C1AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6180682,24.9744151 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-172 | 25-PC-577 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040143 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 486 | Ashik Kasim | 2023-07-17 06:00 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
487 | 812BAA4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6180486,24.9744726 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-303 | 25-PC-578 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-104 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 487 | Ashik Kasim | 2023-07-17 06:07 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
488 | 0B2FAA4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179934,24.974484 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-171 | 25-PC-575 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040185 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 488 | Ashik Kasim | 2023-07-17 06:10 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
489 | CE5AAB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179962,24.974448 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-302 | 25-PC-576 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-114 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 489 | Ashik Kasim | 2023-07-17 06:16 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
490 | 7E2EAA4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179355,24.974483 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-170 | 25-PC-573 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040121 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 490 | Ashik Kasim | 2023-07-17 06:17 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
491 | B4BEAB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179108,24.9744831 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-301 | 25-PC-574 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223892-113 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 491 | Ashik Kasim | 2023-07-17 06:25 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
492 | 492FAA4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.617918,24.9745219 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-315 | 25-PC-568 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-018 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 492 | Ashik Kasim | 2023-07-17 06:36 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
493 | AB5BAB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179504,24.9745237 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LP-314 | 25-PC-606 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-014 | Electrical | Not Available | Gc | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP 18.0003X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 493 | Ashik Kasim | 2023-07-17 06:40 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
494 | 54C0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6178996,24.9744892 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-169 | 25-PC-571 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040362 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 494 | Ashik Kasim | 2023-07-17 08:02 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
495 | 8330AA4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179064,24.9744613 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-168 | 25-PC-569 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040187 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 495 | Ashik Kasim | 2023-07-17 08:05 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
496 | 402FAA4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179025,24.9745421 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-186 | 25-PC-605 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040368 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 496 | Ashik Kasim | 2023-07-17 08:08 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
497 | FF2AAA4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6178985,24.9745432 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-179 | 25-PC-593 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040371 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 497 | Ashik Kasim | 2023-07-17 08:12 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
498 | A82AAA4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.61783,24.974625 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-BAL-304 | 25-PC-592 | Flood Light | EATON | FMVA16LCY-UNV1-76-M20 | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 div 2 | Not Available | T4A | Not Available | 60 | UL | Not Available | Not applicable | Lighting | Periodic | d | Close | A6. Equipment id not available | A6. Fix equipment id |  | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 498 | Ashik Kasim | 2023-07-17 08:23 | A6. Pending | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable
499 | 432CAA4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.617897,24.9745618 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-167 | 25-PC-567 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040345 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 499 | Ashik Kasim | 2023-07-17 08:25 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
500 | 172DAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area | 55.6181483,24.9744803 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SOC-301A | 25-PC-925 | Power Socket-220v/250v | Marechal Electric France | DXA1 2914015 | Not Available | Electrical | 2 | Gb | IEC | Ex de | IIC | T5 | IP66/67 | -55 +60 | LCIE | LCIE15ATEX3033X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 500 | Ashik Kasim | 2023-07-17 08:32 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
501 | 60BEAB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area | 55.6180091,24.9745879 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SJB-101 | 25-PC-724 | Power Socket Junction Box | Weidmuller | Klippon POK 252512 Ex | XB-AE-A-008832 | Electrical | 2 | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IBExU13ATEX1004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 501 | Ashik Kasim | 2023-07-17 08:36 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
502 | D52AAA4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6182872,24.9743863 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-001 | 25-PC-334 | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-046 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close | B6. Broken earth connection | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 502 | Ashik Kasim | 2023-07-17 09:36 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-29 08:39
503 | CB31AA4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6183506,24.9743826 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-050 | 25-PC-333 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040155 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close | A10. Cover bolt loose | A10. Tighten bolts |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 503 | Ashik Kasim | 2023-07-17 09:57 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-29 08:40
504 | 972DAA4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6182317,24.9745314 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-002 | 25-PC-332 | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-008 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close | B6. Broken earth connection | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 504 | Ashik Kasim | 2023-07-17 10:10 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-29 08:59
505 | CF2BAA4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6182037,24.9744902 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-049 | 25-PC-331 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040154 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 505 | Ashik Kasim | 2023-07-17 10:02 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
506 | B92DAA4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6182317,24.9745314 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-003 | 25-PC-352 | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-042 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close | B6. Broken earth connection | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 506 | Ashik Kasim | 2023-07-17 10:13 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-29 09:37
507 | 712FAA4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6182654,24.9745964 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-059 | 25-PC-351 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040175 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 507 | Ashik Kasim | 2023-07-17 10:21 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
508 | 2C2DAA4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.61822,24.9747011 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-004 | 25-PC-328 | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-001 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close | B6. Broken earth connection | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 508 | Ashik Kasim | 2023-07-17 10:33 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-29 09:49
509 | 57C0AB4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.618246,24.9746989 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-047 | 25-PC-327 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040152 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 509 | Ashik Kasim | 2023-07-17 10:35 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
510 | 812DAA4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6182195,24.9747106 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-005 | 25-PC-325 | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-045 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close | B6. Broken earth connection | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 510 | Ashik Kasim | 2023-07-17 10:42 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-29 10:04
511 | 2A89AA4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6182517,24.9746842 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-046 | 25-PC-325 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040196 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 511 | Ashik Kasim | 2023-07-17 10:47 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
512 | A9BFAB4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6181713,24.9748597 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-006 | 25-PC-324 | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-013 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close | B6. Broken earth connection | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 512 | Ashik Kasim | 2023-07-18 05:37 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-29 10:31
513 | 1F2EAA4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6181777,24.9749021 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-045 | 25-PC-323 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040220 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 513 | Ashik Kasim | 2023-07-18 05:40 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
514 | DD2CAA4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6181508,24.9748791 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-007 | 25-PC-350 | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-043 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close | B6. Broken earth connection | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 514 | Ashik Kasim | 2023-07-18 05:47 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-29 11:38
515 | 8C5BAB4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6181812,24.9748905 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-058 | 25-PC-349 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040176 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 515 | Ashik Kasim | 2023-07-18 05:50 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
516 | 882CAA4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6183128,24.9750047 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-008 | 25-PC-344 | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-035 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close | B6. Broken earth connection | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 516 | Ashik Kasim | 2023-07-18 06:03 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-29 11:49
517 | 892BAA4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6181554,24.9749559 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-055 | 25-PC-305 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040176 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 517 | Ashik Kasim | 2023-07-18 06:02 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
518 | 262EAA4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6183051,24.9750325 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-009 | 25-PC-342 | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-041 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 518 | Ashik Kasim | 2023-07-18 06:11 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
519 | C931AA4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6182561,24.9751128 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-054 | 25-PC-341 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040241 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 519 | Ashik Kasim | 2023-07-18 06:14 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
520 | E52BAA4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6182375,24.9752817 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-010 | 25-PC-318 | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-037 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 520 | Ashik Kasim | 2023-07-18 06:22 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
521 | F462AB4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6182183,24.9752493 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-042 | 25-PC-317 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040159 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 521 | Ashik Kasim | 2023-07-18 06:27 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
522 | E52FAA4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6182459,24.975273 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-011 | 25-PC-316 | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-039 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 522 | Ashik Kasim | 2023-07-18 06:31 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
523 | 7259AB4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6182605,24.9753625 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-041 | 25-PC-315 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040213 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 523 | Ashik Kasim | 2023-07-18 06:41 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
524 | A22AAA4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6182344,24.9752668 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-012 | 25-PC-338 | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-034 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 524 | Ashik Kasim | 2023-07-18 08:13 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
525 | BA2DAA4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.618217,24.9752607 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-052 | 25-PC-337 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040209 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 525 | Ashik Kasim | 2023-07-18 08:15 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
526 | 902BAA4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6182607,24.9752979 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PAL-013 | 25-PC-312 | LED Pendant Light Fixture | EATON | LPL18-C57--9L-V07-1M-LT1-CG | 62703160-015 | Electrical | Not Available | Gb | IEC | Ex db ec | IIC | T6 | IP66 | -40 +55 | CQM | IECEx CQM16.0043X | Yes | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 526 | Ashik Kasim | 2023-07-18 08:21 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
527 | 0B5EAB4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6182263,24.9753493 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-039 | 25-PC-311 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040280 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 527 | Ashik Kasim | 2023-07-18 08:26 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
528 | 362BAA4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6182084,24.9752792 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-UJBS-2512 | CA_25-FYIFZT-102 | Junction Box | Weidmuller | MH453820S4N1 | XB-AE-A-039880 | Electrical | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 528 | Ashik Kasim | 2023-07-18 09:07 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
529 | AF2BAA4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6182791,24.9752235 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-UJBS-2513 | CD_25-UJBD-2513 | Junction Box | Weidmuller | MH453820S4N1 | XB-AE-A-039940 | Electrical | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 529 | Ashik Kasim | 2023-07-18 09:07 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
530 | 3C8BAA4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6182209,24.9752457 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-UJBS-2514 | CD_25-UJBD-2514-01 | Junction Box | Weidmuller | MH453820S4N1 | XB-AE-A-039913 | Electrical | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 530 | Ashik Kasim | 2023-07-18 09:10 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
531 | F52AAA4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.618298,24.9753361 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-DJBS-2512 | CD_25-DJBD-2512 | Junction Box | Weidmuller | MH453820S4N1 | XB-AE-A-039894 | Electrical | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 531 | Ashik Kasim | 2023-07-18 09:14 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
532 | 342BAA4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6182503,24.9752377 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FJBS-2512 | CA_25-FJBS-2512 | Junction Box | Weidmuller | MH453820S4N1 | XB-AE-A-039920 | Electrical | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 532 | Ashik Kasim | 2023-07-18 09:19 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
533 | 8A2CAA4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6181848,24.9752631 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-EJBD-2502 | CD_25-EJBD-2502 | Junction Box | Weidmuller | MH453820S4N1 | XB-AE-A-039885 | Electrical | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 533 | Ashik Kasim | 2023-07-18 09:22 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
534 | A62FAA4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.61819,24.9751428 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-DJBD-2514 | CD_25-DJBD-2514 | Junction Box | Weidmuller | MH453820S4N1 | XB-AE-A-039826 | Electrical | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 534 | Ashik Kasim | 2023-07-18 09:26 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
535 | 6D59AB4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6182516,24.9751144 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-DJBD-2513 | CD_25-DJBD-2513 | Junction Box | Weidmuller | MH453820S4N1 | XB-AE-A-039935 | Electrical | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 535 | Ashik Kasim | 2023-07-18 09:29 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
536 | B557AB4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6182135,24.9751038 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-DJBD-2502 | CD_25-DJBD-2502 | Junction Box | Weidmuller | MH453820S4N1 | XB-AE-A-039905 | Electrical | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 536 | Ashik Kasim | 2023-07-18 09:32 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
537 | 4B2DAA4E080104E0 |  | Margham | Area 25 | MEC Pipeline area | 55.6182775,24.9750655 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-UJBD-2515 | CD_25-UJBD-2515 | Junction Box | Weidmuller | MH453820S4N1 | XB-AE-A-039890 | Electrical | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 537 | Ashik Kasim | 2023-07-18 09:37 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
538 | F888AA4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.618222,24.9750604 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-VJBD-2512 | CD_25-VJBD-2512 | Junction Box - Vibration Switch | STAHL | 8150/1-0200-0300-150-3321 | Not Available | Electrical | 2 | Gb | IEC | Ex eb | IIC | T4 | IP66 | -60 +70 | PTB | PTB09ATEX1108 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 538 | Ashik Kasim | 2023-07-18 09:51 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
539 | 502EAA4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6183656,24.9750285 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-VJBD-2511 | CD_25-VJBD-2511 | Junction Box - Vibration Switch | STAHL | 8150/1-0200-0300-150-3321 | Not Available | Electrical | 2 | Gb | IEC | Ex eb | IIC | T4 | IP66 | -60 +70 | PTB | PTB09ATEX1108 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 539 | Ashik Kasim | 2023-07-18 09:57 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
540 | BB30AA4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6181361,24.9753933 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-105 | CA_25-TIT-105 | Temperature Transmitter | Rosemount | 3144PD1A2E7B4M5CNC4Q4U1QTXAK1105 | 3587948 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECExFMG12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 540 | Ashik Kasim | 2023-07-18 10:08 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
541 | 6D2BAA4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6182904,24.9752018 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-100 | CA_25-TIT-100 | Temperature Transmitter | Rosemount | 3144PD1A2E7B4M5CNC4Q4U1QTXAK1105 | 3587935 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECExFMG12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 541 | Ashik Kasim | 2023-07-18 10:11 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
542 | FFC0AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6182722,24.9751704 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-100 | CA_25-PIT-100 | Pressure Transmitter | Rosemount | 3051SAAD1E7M5 | 0942215 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECExKEM08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 542 | Ashik Kasim | 2023-07-18 10:26 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
543 | 7C2EAA4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6182157,24.9751816 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FIT-100 | CA_25-FIT-100 | Flow Transmitter | Rosemount | 300S1AAD1E7M5 | Not visible | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECExKEM08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 543 | Ashik Kasim | 2023-07-18 10:50 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
544 | 1430AA4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6185099,24.9756188 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LCS-101A | 25-CC-056 | LCS- Exd Enclosure | BARTEC | 19D1009s/01 | 3937544-10-21 | Electrical | 2 | Gb | IEC | Ex db | IIB+H2 | T6 | IP66 | -5 +58 | DEKRA | DEKRA 13ATEX0209 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 544 | Ashik Kasim | 2023-07-19 05:39 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
545 | 8DBEAB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6185099,24.9756188 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LCS-101C | 25-CC-062 | LCS- Exd Enclosure | BARTEC | 19D1009s/01 | 3937544-10-09 | Electrical | 2 | Gb | IEC | Ex db | IIB+H2 | T6 | IP66 | -5 +58 | DEKRA | DEKRA 13ATEX0209 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 545 | Ashik Kasim | 2023-07-19 05:41 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
546 | A35DAB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6184552,24.9753456 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LCS-101E | 25-CC-068 | LCS- Exd Enclosure | BARTEC | 19D1009s/01 | 3937544-10-03 | Electrical | 2 | Gb | IEC | Ex db | IIB+H2 | T6 | IP66 | -5 +58 | DEKRA | DEKRA 13ATEX0209 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 546 | Ashik Kasim | 2023-07-19 05:43 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
547 | 772CAA4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6185346,24.9753017 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LCS-101B | 25-CC-059 | LCS- Exd Enclosure | BARTEC | 19D1009s/01 | 3937544-10-07 | Electrical | 2 | Gb | IEC | Ex db | IIB+H2 | T6 | IP66 | -5 +58 | DEKRA | DEKRA 13ATEX0209 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 547 | Ashik Kasim | 2023-07-19 05:46 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
548 | AD2CAA4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6182816,24.9751808 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LCS-101D | 25-CC-065 | LCS- Exd Enclosure | BARTEC | 19D1009s/01 | 3937544-10-20 | Electrical | 2 | Gb | IEC | Ex db | IIB+H2 | T6 | IP66 | -5 +58 | DEKRA | DEKRA 13ATEX0209 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 548 | Ashik Kasim | 2023-07-19 05:48 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
549 | D42BAA4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6183822,24.9751933 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LCS-101F | 25-CC-071 | LCS- Exd Enclosure | BARTEC | 19D1009s/01 | 3937544-10-11 | Electrical | 2 | Gb | IEC | Ex db | IIB+H2 | T6 | IP66 | -5 +58 | DEKRA | DEKRA 13ATEX0209 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 549 | Ashik Kasim | 2023-07-19 05:50 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
550 | AF30AA4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6185012,24.9751809 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LCS-102A | 25-CC-074 | LCS- Exd Enclosure | BARTEC | 19D1009s/01 | 3937544-10-16 | Electrical | 2 | Gb | IEC | Ex db | IIB+H2 | T6 | IP66 | -5 +58 | DEKRA | DEKRA 13ATEX0209 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 550 | Ashik Kasim | 2023-07-19 05:53 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
551 | EB2DAA4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6185527,24.9750646 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LCS-102B | 25-CC-077 | LCS- Exd Enclosure | BARTEC | 19D1009s/01 | 3937544-10-05 | Electrical | 2 | Gb | IEC | Ex db | IIB+H2 | T6 | IP66 | -5 +58 | DEKRA | DEKRA 13ATEX0209 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 551 | Ashik Kasim | 2023-07-19 05:55 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
552 | C58BAA4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6184022,24.9750078 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LCS-102C | 25-CC-080 | LCS- Exd Enclosure | BARTEC | 19D1009s/01 | 3937544-10-04 | Electrical | 2 | Gb | IEC | Ex db | IIB+H2 | T6 | IP66 | -5 +58 | DEKRA | DEKRA 13ATEX0209 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 552 | Ashik Kasim | 2023-07-19 06:00 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
553 | 7930AA4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6186949,24.9750911 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-102C | 25-PC-069A | Ex d On/Off Switch | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440024 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 553 | Ashik Kasim | 2023-07-19 06:08 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
554 | B12BAA4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6185185,24.9750085 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-102B | 25-PC-067A | Ex d On/Off Switch | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440032 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 554 | Ashik Kasim | 2023-07-19 06:11 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
555 | DFBEAB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6184329,24.9750797 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-102A | 25-PC-065A | Ex d On/Off Switch | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440036 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 555 | Ashik Kasim | 2023-07-19 06:14 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
556 | 052EAA4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6184374,24.9751222 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-101F | 25-PC-063A | Ex d On/Off Switch | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440029 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 556 | Ashik Kasim | 2023-07-19 06:16 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
557 | 2B2DAA4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.618428,24.9751764 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-101D | 25-PC-059A | Ex d On/Off Switch | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440014 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 557 | Ashik Kasim | 2023-07-19 06:20 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
558 | 4730AA4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6184478,24.9751969 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-101B | 25-PC-055A | Ex d On/Off Switch | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440031 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 558 | Ashik Kasim | 2023-07-19 06:22 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
559 | E5BEAB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6184586,24.9753098 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-101E | 25-PC-061A | Ex d On/Off Switch | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440016 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 559 | Ashik Kasim | 2023-07-19 06:23 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
560 | 8057AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6184532,24.9753546 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-101C | 25-PC-057A | Ex d On/Off Switch | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440011 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 560 | Ashik Kasim | 2023-07-19 06:26 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
561 | 872CAA4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6184228,24.975264 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-101A | 25-PC-053A | Ex d On/Off Switch | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440022 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 561 | Ashik Kasim | 2023-07-19 06:29 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
562 | 5E2DAA4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6184402,24.975349 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FJBD-2503 | CD_25-FJBD-2503 | Junction Box | Weidmuller | MH453820S4N1 | XB-AE-A-039899 | Electrical | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 562 | Ashik Kasim | 2023-07-19 06:34 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
563 | E22FAA4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6182535,24.9748668 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HS-2529 | CD_25-HS-2529 | Emergency Hand switch | EATON | SM87PBLD | 2156859197112 | Instrumentation | Not Available | Gb | IEC | Ex d | IIC | T5 | IP66/67 | -55 +70 | BAS | IECEx BAS 09.0060 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 563 | Ashik Kasim | 2023-07-19 08:12 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
564 | 1C2CAA4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6185407,24.9749919 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HS-2518 | CD_25-HS-2518 | Emergency Hand switch | EATON | SM87PBLD | 2156859197107 | Instrumentation | Not Available | Gb | IEC | Ex d | IIC | T5 | IP66/67 | -55 +70 | BAS | IECEx BAS 09.0060 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 564 | Ashik Kasim | 2023-07-19 08:14 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
565 | 222EAA4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6185407,24.9749919 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HS-2543 | CD_25-HS-2543 | Emergency Hand switch | EATON | SM87PBLD | 215685919 71 04 | Instrumentation | Not Available | Gb | IEC | Ex d | IIC | T5 | IP66/67 | -55 +70 | BAS | IECEx BAS 09.0060 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 565 | Ashik Kasim | 2023-07-19 08:19 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
566 | 532BAA4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6183518,24.9752993 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HS-2519 | CD_25-HS-2519 | Emergency Hand switch | EATON | SM87PBLD | 215685919 71 08 | Instrumentation | Not Available | Gb | IEC | Ex d | IIC | T5 | IP66/67 | -55 +70 | BAS | IECEx BAS 09.0060 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 566 | Ashik Kasim | 2023-07-19 08:23 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
567 | BC5DAB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area-Ground | 55.6181857,24.9751748 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-DJBS-2511 | CA_25-DJBS-2511 | Junction Box | Weidmuller | MH453820S4N1 | XB-AE-A-039887 | Electrical | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 567 | Ashik Kasim | 2023-07-19 08:26 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
568 | CF2CAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area-Ground | 55.618074,24.9752737 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-DJBD-2512 | CD_25-DJBD-2512 | Junction Box | Weidmuller | MH453820S4N1 | XB-AE-A-039925 | Electrical | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 568 | Ashik Kasim | 2023-07-19 08:29 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
569 | 192FAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area-Ground | 55.6181326,24.9752383 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-DJBD-2511 | CD_25-DJBD-2511 | Junction Box | Weidmuller | MH453820S4N1 | XB-AE-A-039934 | Electrical | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 569 | Ashik Kasim | 2023-07-19 08:31 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
570 | 652BAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area-Ground | 55.6181408,24.9751826 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FJBD-2511 | CD_25-FJBD-2511 | Junction Box | Weidmuller | MH453820S4N1 | XB-AE-A-039900 | Electrical | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 570 | Ashik Kasim | 2023-07-19 08:34 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
571 | BDBEAB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area-Ground | 55.6180984,24.9751883 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-UJBD-2512 | CD_25-UJBD-2512-02 | Junction Box | Weidmuller | MH453820S4N1 | XB-AE-A-039931 | Electrical | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 571 | Ashik Kasim | 2023-07-19 08:39 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
572 | 052CAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area-Ground | 55.6180452,24.9752298 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-UJBS-2513 | CD_25-UJBS-2513 | Junction Box | Weidmuller | MH453820S4N1 | XB-AE-A-039945 | Electrical | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 572 | Ashik Kasim | 2023-07-19 08:42 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
573 | 552CAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area-Ground | 55.6179646,24.9751573 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FJBS-2511 | CA_25-FjBS-2511 | Junction Box | Weidmuller | MH453820S4N1 | XB-AE-A-039919 | Electrical | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 573 | Ashik Kasim | 2023-07-19 08:47 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
574 | FE2CAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area-Ground | 55.6178329,24.9751819 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-UJBS-2511 | CA_25-UjBS-2511 | Junction Box | Weidmuller | MH453820S4N1 | XB-AE-A-039944 | Electrical | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 574 | Ashik Kasim | 2023-07-19 08:55 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
575 | 4630AA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area-Ground | 55.6181126,24.9750244 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-UJBD-2511 | CD_25-UjBD-2511 | Junction Box | Weidmuller | MH453820S4N1 | XB-AE-A-039916 | Electrical | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 575 | Ashik Kasim | 2023-07-19 08:59 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
576 | 412FAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area-Ground | 55.6181166,24.9750371 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HS-2517 | CD_25-HS-2517 | Emergency Hand switch | EATON | SM87PBLD | 215685919 71 06 | Instrumentation | Not Available | Gb | IEC | Ex d | IIC | T5 | IP66/67 | -55 +70 | BAS | IECEx BAS 09.0060 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 576 | Ashik Kasim | 2023-07-19 09:14 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
577 | 4C5CAB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.618109,24.9750884 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PDIT-2511 | CA_25-PDIT-2511 | DP TRANSMITTER, 25-XV-2561 | Rosemount | 300S1AAD1E7M5 | 942294 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T5 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 577 | Ashik Kasim | 2023-07-20 05:41 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
578 | 38C1AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6181256,24.9751088 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-2561 | CD_25-XY-2561 | SOLENOID VALVE, SHUTDOWN VALVE 25-MOV-2511 BYPASS LINE | Bifold | FP06P-77A | FL10919-0378 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 578 | Ashik Kasim | 2023-07-20 05:48 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
579 | 8EBEAB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6181654,24.9750961 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZSC-2561/25-ZSO-2561 | CD_25-ZS-2561 | POSITION SWITCH, SHUTDOWN VALVE 25-MOV-2511 BYPASS LINE | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 579 | Ashik Kasim | 2023-07-20 06:07 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
580 | E2BEAB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6181627,24.9750664 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-2511 | CD_25-MOV-2511 | MOTOR OPERATED VALVE 25-MOV-2511 | BIFFI | WGR3200 + ICON-020/180-144 (3000 Series) | 192273E021001 | Electrical | Not Available | Gb | IEC | Ex d. h ia | IIB | T4 | IP66/68 | -20 +85 | INE | IECEx INE 18.0026X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 580 | Ashik Kasim | 2023-07-20 06:22 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
581 | C52CAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6181742,24.9750752 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-2511-ISO | 25-PC-115A | ISOLATOR, MOTOR OPERATED VALVE 25-MOV-2511 | TECHNOR | CPSG-26/EFSRC-420 | 20P0092450010 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 581 | Ashik Kasim | 2023-07-20 06:27 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
582 | D3C1AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6182047,24.9750929 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-2512-ISO | 25-PC-116A | ISOLATOR, MOTOR OPERATED VALVE 25-MOV-2512 | TECHNOR | CPSG-26/EFSRC-420 | 20P0092450011 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 582 | Ashik Kasim | 2023-07-20 06:30 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
583 | 995AAB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6181627,24.9750664 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-2512 | CD_25-MOV-2512 | MOTOR OPERATED VALVE 25-MOV-2512 | BIFFI | WGR3200 + ICON-020/180-144 (3000 Series) | 192273E020001 | Electrical | Not Available | Gb | IEC | Ex d. h ia | IIB | T4 | IP66/68 | -20 +85 | INE | IECEx INE 18.0026X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 583 | Ashik Kasim | 2023-07-20 06:34 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
584 | 41C0AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6181507,24.9751067 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZSC-2562/25-ZSO-2562 | CD_25-ZS-2562 | POSITION SWITCH, SHUTDOWN VALVE 25-MOV-2512 BYPASS LINE | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 584 | Ashik Kasim | 2023-07-20 06:40 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
585 | D0BFAB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6181302,24.9751528 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-2562 | CD_25-XY-2562 | SOLENOID VALVE, SHUTDOWN VALVE 25-MOV-2512 BYPASS LINE | Bifold | FP06P-77A | FL10919-0363 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 585 | Ashik Kasim | 2023-07-20 06:41 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
586 | B0C0AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6182058,24.9751434 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PDIT-2512 | CA_25-PDIT-2512 | DP TRANSMITTER, 25-XV-2561 | Rosemount | 300S1AAD1E7M5 | 942289 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T5 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 586 | Ashik Kasim | 2023-07-20 06:47 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
587 | 4AC1AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6182368,24.9751075 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PDIT-100 | CA_25-PDIT-100 | DP TRANSMITTER, 25-XV-101 | Rosemount | 300S1AAD1E7M5 | Not visible | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T5 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 587 | Ashik Kasim | 2023-07-20 08:07 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
588 | 51C4AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6181419,24.9750595 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-2562 | CD_25-XY-2562 | SOLENOID VALVE, EQUALIZING VALVE ACROSS 25-XV-100 | Bifold | FP06P-77A | FL10919-0381 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 588 | Ashik Kasim | 2023-07-20 08:10 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
589 | C7BEAB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6181133,24.9750592 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZSC-101/25-ZSO-101 | CD_25-ZS-101 | POSITION SWITCH, SHUTDOWN VALVE 25-MOV-101 BYPASS LINE | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 589 | Ashik Kasim | 2023-07-20 08:15 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
590 | A9C1AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6180489,24.9751183 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-116-ISO | 25-PC-106A | ISOLATOR, MOTOR OPERATED VALVE 25-MOV-116 | TECHNOR | CPSG-26/EFSRC-420 | 20P0092450018 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 590 | Ashik Kasim | 2023-07-20 08:21 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
591 | B1C1AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6180013,24.9751012 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-116 | CD_25-MOV-116 | MOTOR OPERATED VALVE 25-MOV-116 | BIFFI | WGR3200 + ICON-020/180-144 (3000 Series) | 192273E009001 | Electrical | Not Available | Gb | IEC | Ex d. h ia | IIB | T4 | IP66/68 | -20 +85 | INE | IECEx INE 18.0026X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 591 | Ashik Kasim | 2023-07-20 08:27 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
592 | E9C3AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179839,24.9751261 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-104C | CA_25-TIT-104C | TEMPERATURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 1 - HP SECTION | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 3587947 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 592 | Ashik Kasim | 2023-07-20 08:39 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
593 | F8C1AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179419,24.9751303 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-104B | CA_25-TIT-104B | TEMPERATURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 1 - HP SECTION | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 3587946 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 593 | Ashik Kasim | 2023-07-20 08:41 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
594 | CCC2AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179334,24.9751122 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-104A | CA_25-TIT-104A | TEMPERATURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 1 - HP SECTION | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 3587945 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 594 | Ashik Kasim | 2023-07-20 08:44 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
595 | EAC0AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179391,24.9751345 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-104C | CA_25-PIT-104C | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 1 - HP SECTION | Rosemount | 300S1AAD1E7M5 | 0942196 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 595 | Ashik Kasim | 2023-07-20 08:44 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
596 | A3BFAB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179569,24.9751462 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-104B | CA_25-PIT-104B | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 1 - HP SECTION | Rosemount | 300S1AAD1E7M5 | 0942195 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 596 | Ashik Kasim | 2023-07-20 08:56 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
597 | 8EC1AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.617966,24.9751524 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-104A | CA_25-PIT-104A | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 1 - HP SECTION | Rosemount | 300S1AAD1E7M5 | Not visible | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 597 | Ashik Kasim | 2023-07-20 08:59 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
598 | 23C3AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179362,24.9751248 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-108 | CA_25-TIT-108 | TEMPERATURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 1 - HP SECTION | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 3587944 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 598 | Ashik Kasim | 2023-07-20 09:03 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
599 | B72BAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6180029,24.9751146 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-106 | CA_25-PIT-106 | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 1 - HP SECTION | Rosemount | 300S1AAD1E7M5 | 0942195 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 599 | Ashik Kasim | 2023-07-20 09:08 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
600 | EB2FAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179338,24.9751424 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-103 | CA_25-TIT-103 | TEMPERATURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 1 - HP SECTION | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 0944303 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 600 | Ashik Kasim | 2023-07-20 09:25 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
601 | 2130AA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179561,24.9751142 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-109 | CA_25-PIT-109 | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 1 - HP SECTION | Rosemount | 300S1AAD1E7M5 | 942193 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 601 | Ashik Kasim | 2023-07-20 09:28 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
602 | F0C1AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.61794,24.9751288 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-108 | CA_25-PIT-108 | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 1 - HP SECTION | Rosemount | 300S1AAD1E7M5 | 942192 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 602 | Ashik Kasim | 2023-07-20 09:31 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
603 | DA2CAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179625,24.9751017 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-103 | CA_25-PIT-103 | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 1 - HP SECTION | Rosemount | Not Available | 0500053 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 603 | Ashik Kasim | 2023-07-20 09:37 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
604 | 5EC1AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179518,24.9751116 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-101 | CA_25-PIT-101 | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 1 - HP SECTION | Rosemount | Not Available | 0500052 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 604 | Ashik Kasim | 2023-07-20 09:47 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
605 | EA2AAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.617917,24.9750947 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-107 | CA_25-PIT-107 | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 1 - HP SECTION | Rosemount | 300S1AAD1E7M5 | 942182 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 605 | Ashik Kasim | 2023-07-20 09:50 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
606 | F22DAA4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179263,24.9751316 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-101 | CA_25-TIT-101 | TEMPERATURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 1 - HP SECTION | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 3587939 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 606 | Ashik Kasim | 2023-07-20 09:57 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
607 | 3D5EAB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179896,24.9751321 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2514 | CA_25-AE-2514 | FLAMMABLE GAS DETECTOR - IR POINT TYPE | Net Safety | SC311S-100-ASSY | 0085904 | Instrumentation | Not Available | Gb | IEC | Ex db | IIB + H2 | T5 | IP64 | -40 +75 | FMG | IECEx FMG 12.0007X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 607 | Ashik Kasim | 2023-07-20 10:07 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
608 | 7BBFAB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179754,24.9751795 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-BAL-104 | 25-PC-276 | Flood Light | EATON | FMVA16LCY-UNV1-76-M20 | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 div 2 | Not Available | T4A | Not Available | 60 | UL | Not Available | Not applicable | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 608 | Ashik Kasim | 2023-07-20 10:28 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
609 | 01C2AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6178766,24.9751497 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-021 | 25-PC-277 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040343 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close | A4. Perished IP Washer | A4. Replace IP Washer |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 609 | Ashik Kasim | 2023-07-20 10:27 | A4. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-09-04 10:24
610 | C35AAB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6178892,24.9750804 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-102C | CA_25-TIT-102C | TEMPERATURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 1 - LP SECTION | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 3587943 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 610 | Ashik Kasim | 2023-07-21 05:49 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
611 | C0C3AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179263,24.9751217 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-102B | CA_25-TIT-102B | TEMPERATURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 1 - LP SECTION | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 3587942 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close | B6. Broken earth connection | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 611 | Ashik Kasim | 2023-07-21 05:53 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-24 05:49
612 | 78C1AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.617917,24.9750778 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-102A | CA_25-TIT-102A | TEMPERATURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 1 - LP SECTION | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 3587938 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 612 | Ashik Kasim | 2023-07-21 05:55 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
613 | CEBFAB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179392,24.9750715 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-102C | CA_25-PIT-102C | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 1 - LP SECTION | Rosemount | 300S1AAD1E7M5 | 942191 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 613 | Ashik Kasim | 2023-07-21 05:59 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
614 | 2AC2AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179303,24.9751109 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-102B | CA_25-PIT-102B | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 1 - LP SECTION | Rosemount | 300S1AAD1E7M5 | 942184 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 614 | Ashik Kasim | 2023-07-21 06:01 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
615 | 3EC0AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179266,24.9751177 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-102A | CA_25-PIT-102A | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 1 - LP SECTION | Rosemount | 300S1AAD1E7M5 | 942183 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 615 | Ashik Kasim | 2023-07-21 06:05 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
616 | D8BFAB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179231,24.9751197 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-107 | CA_25-TIT-107 | TEMPERATURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 1 - LP SECTION | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 3587941 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 616 | Ashik Kasim | 2023-07-21 06:07 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
617 | 4EC1AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179001,24.9751301 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-105 | CA_25-PIT-105 | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 1 - LP SECTION | Rosemount | Not Available | 0500179 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 617 | Ashik Kasim | 2023-07-21 06:11 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
618 | F3C0AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179875,24.9750663 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FIT-102B | CA_25-FIT-102B | FLOW TRANSMITTER, MULTI ENVELOPE COMPRESSOR 1 - HP SECTION | Rosemount | Not Available | 0500189 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 09.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 618 | Ashik Kasim | 2023-07-21 06:17 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
619 | 24C3AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179535,24.9750858 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FIT-102A | CA_25-FIT-102A | FLOW TRANSMITTER, MULTI ENVELOPE COMPRESSOR 1 - HP SECTION | Rosemount | Not Available | 0500183 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 09.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 619 | Ashik Kasim | 2023-07-21 06:19 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
620 | 91C1AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179573,24.9750697 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FIT-101A | CA_25-FIT-101A | FLOW TRANSMITTER, MULTI ENVELOPE COMPRESSOR 1 - LP SECTION | Rosemount | Not Available | 0500183 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 09.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 620 | Ashik Kasim | 2023-07-21 06:21 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
621 | EFC3AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179519,24.9750816 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FIT-101B | CA_25-FIT-101B | FLOW TRANSMITTER, MULTI ENVELOPE COMPRESSOR 1 - LP SECTION | Rosemount | Not Available | 0500188 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 09.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 621 | Ashik Kasim | 2023-07-21 06:23 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
622 | 8B63AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.617966,24.9750765 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PDIT-101 | CA_25-PDIT-101 | DP TRANSMITTER, 25-C-101 LP SECTION INLET FILTER | Rosemount | 300S1AAD1E7M5 | 0942295 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T5 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 622 | Ashik Kasim | 2023-07-21 06:27 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
623 | 8FC1AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179466,24.9750476 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PDIT-102 | CA_25-PDIT-102 | DP TRANSMITTER, 25-C-101 LP SECTION INLET FILTER | Rosemount | 300S1AAD1E7M5 | 0942296 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T5 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 623 | Ashik Kasim | 2023-07-21 06:32 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
624 | 54C1AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6177934,24.974965 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2515T | CA_25-AE-2515T | FLAMMABLE GAS DETECTOR - OPEN PATH TYPE TRANSMITTER | Safe Eye | Quasar 900 | Not available | Instrumentation | Not Available | Gb | IEC | Ex db eb ib | Not stated | T4 | Not Visible | -55 +50 | Sira | 00ATEX1182X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 624 | Ashik Kasim | 2023-07-21 08:25 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
625 | 27C0AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179776,24.9750981 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FZSO-104/25-FZSC-104 | CD_25-ZS-104 | POSITION SWITCH , MEC 1 HOT GAS BYPASS VALVE- LP STAGE 25-XY-104 | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close | A6. Equipment id not available | A6. Fix equipment id |  | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 625 | Ashik Kasim | 2023-07-21 08:48 | A6. Pending | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable
626 | C3C2AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179847,24.9750883 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-104 | CD_25-XY-104 | SOLENOID VALVE, MEC 1 HOT GAS BYPASS VALVE- LP STAGE- 25-XV-104 | ASCO | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex d | IIC | T6 | IP67 | -50 +60 | LCIE | IECEx LCIE07.0015X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 626 | Ashik Kasim | 2023-07-21 09:01 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
627 | 96C1AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179993,24.9751033 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FZSO-105/25-FZSC-105 | CD_25-ZS-105 | POSITION SWITCH , MEC 1 HOT GAS BYPASS VALVE- HP STAGE 25-XY-105 | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 627 | Ashik Kasim | 2023-07-21 09:14 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
628 | 465EAB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6179847,24.9750883 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-105 | CD_25-XY-105 | SOLENOID VALVE, MEC 1 HOT GAS BYPASS VALVE- LP STAGE- 25-XV-105 | ASCO | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex d | IIC | T6 | IP67 | -50 +60 | LCIE | IECEx LCIE07.0015X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 628 | Ashik Kasim | 2023-07-21 09:20 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
629 | 2DC3AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6180602,24.9751198 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZSO-100/25-ZSC-100 | CD_25-ZS-100 | POSITION SWITCH , SHUTDOWN VALVE INLET MEC-1 (25-C-101/102) | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 629 | Ashik Kasim | 2023-07-21 09:31 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
630 | 20C1AB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.61817,24.9750833 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-100 | CD_25-XY-100 | SOLENOID VALVE, SHUTDOWN VALVE INLET MEC-1 (25-C-101/102) | Bifold | FP06P-77A | FL10919-0361 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 630 | Ashik Kasim | 2023-07-21 09:35 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
631 | DFBFAB4E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Area (+15) | 55.6181478,24.9750927 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2515R | CA_25-AE-2515R | FLAMMABLE GAS DETECTOR - OPEN PATH RECEIVER | Safe Eye | Quasar 900 | Not available | Instrumentation | Not Available | Gb | IEC | Ex db eb ib | Not stated | T4 | Not Visible | -55 +50 | Sira | IECEx SIR 13.0069X | Yes | Others | Periodic | d | Close | A10. Wrong type blanking elements installed | A10. Replace with suitable type blanking elements |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 631 | Ashik Kasim | 2023-07-21 09:48 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Not Applicable | Ashik Kasim | 2023-08-28 08:45
632 | B7C1AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6183197,24.9750368 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-2511 | CA_25-PIT-2511 | PRESSURE TRANSMITTER, AREA 25 COMPRESSOR A | Rosemount | 300S1AAD1E7M5 | 0942119 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T5 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close | B6. Broken earth connection | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 632 | Ashik Kasim | 2023-07-21 10:15 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-17 10:38
633 | BBBEAB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6180013,24.9751012 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-2514 | CD_25-MOV-2514 | MOV - 25-E-101/2 A/B OUTLET TO MEC INTERCONNECTION HEADER | BIFFI | WGR3200 + ICON-020/180-144 (3000 Series) | 192273E008001 | Electrical | Not Available | Gb | IEC | Ex d. h ia | IIB | T4 | IP66/68 | -20 +85 | INE | IECEx INE 18.0026X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 633 | Ashik Kasim | 2023-07-21 10:23 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
634 | 89C0AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6183491,24.975063 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-2514-ISO | 25-PC-118A | ISOLATOR, MOTOR OPERATED VALVE 25-MOV-2514 | TECHNOR | CPSG-26/EFSRC-420 | 20P0092450009 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 634 | Ashik Kasim | 2023-07-21 10:27 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
635 | 9CC0AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6182515,24.9750777 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZSO-2564/25-ZSC-2564 | CD_25-ZS-2564 | POSITION SWITCH , SHUTDOWN VALVE 25-MOV-2514 BYPASS LINE | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 635 | Ashik Kasim | 2023-07-21 10:33 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
636 | A0BFAB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6182869,24.9750886 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-2564 | CD_25-XY-2564 | SOLENOID VALVE, SHUTDOWN VALVE 25-MOV-2514 BYPASS LINE | Bifold | FP06P-77A | FL10919-0394 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 636 | Ashik Kasim | 2023-07-21 10:37 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
637 | E9C1AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6183037,24.9750953 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZSO-2563/25-ZSC-2563 | CD_25-ZS-2563 | POSITION SWITCH , SHUTDOWN VALVE 25-MOV-2513 BYPASS LINE | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 637 | Ashik Kasim | 2023-07-21 10:42 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
638 | 93BEAB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6182879,24.9751171 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-2563 | CD_25-XY-2563 | SOLENOID VALVE, SHUTDOWN VALVE 25-MOV-2513 BYPASS LINE | Bifold | FP06P-77A | FL10919-0369 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 638 | Ashik Kasim | 2023-07-21 10:45 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
639 | 7D5DAB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6183217,24.9751083 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-2513 | CD_25-MOV-2513 | MOV - 25-E-101/2 A/B OUTLET TO MEC DISCHARGE HEADER | BIFFI | WGR3200 + ICON-020/180-144 (3000 Series) | 192273E009001 | Electrical | Not Available | Gb | IEC | Ex d. h ia | IIB | T4 | IP66/68 | -20 +85 | INE | IECEx INE 18.0026X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 639 | Ashik Kasim | 2023-07-21 10:48 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
640 | 915AAB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6183265,24.975146 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-2513-ISO | 25-PC-117A | ISOLATOR, MOTOR OPERATED VALVE 25-MOV-2513 | TECHNOR | CPSG-26/EFSRC-420 | 20P0092450005 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 640 | Ashik Kasim | 2023-07-21 10:51 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
641 | 8ABFAB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6184371,24.9751733 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-2510 | CD_25-XY-2510 | SOLENOID VALVE, BLOWDOWN VALVE MEC INTERCONNECTION HEADER | Bifold | FP06P-77A | FL10919-0373 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 641 | Ashik Kasim | 2023-07-24 05:35 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
642 | BEBEAB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6183185,24.9750911 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZSO-2510/25-ZSC-2510 | CD_25-ZS-2510 | POSITION SWITCH, BLOWDOWN VALVE MEC INTERCONNECTION HEADER | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 642 | Ashik Kasim | 2023-07-24 05:38 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
643 | C0C4AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6183203,24.9752207 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-108 | CD_25-XY-108 | SOLENOID VALVE, BLOWDOWN VALVE PROCESS GAS COOLER OUTLET (25-E-102 A/B) | Bifold | FP06P-77A | FL10919-0379 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 643 | Ashik Kasim | 2023-07-24 05:42 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
644 | EF2BAA4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6183234,24.9751799 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZSC-108/25-ZSO-108 | CD_25-ZS-108 | POSITION SWITCH , BLOWDOWN VALVE PROCESS GAS COOLER OUTLET (25-E-102 A/B) | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 644 | Ashik Kasim | 2023-07-24 05:48 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
645 | 77BFAB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.618301,24.975181 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-117 | CD_25-MOV-117 | MOV - PROCESS GAS COOLER OUTLET (25-E-101 A/B ) TO 25-C-102 | BIFFI | WGR3200 + ICON-020/180-144 (3000 Series) | 192273E008001 | Electrical | Not Available | Gb | IEC | Ex d. h ia | IIB | T4 | IP66/68 | -20 +85 | INE | IECEx INE 18.0026X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 645 | Ashik Kasim | 2023-07-24 05:52 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
646 | 43C2AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6182972,24.9751742 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-107-ISO | 25-PC-107A | ISOLATOR, MOTOR OPERATED VALVE 25-MOV-117 | TECHNOR | CPSG-26/EFSRC-420 | 20P0092450015 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 646 | Ashik Kasim | 2023-07-24 05:56 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
647 | 1BC5AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6183026,24.9752317 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-118 | CD_25-MOV-118 | MOV -PROCESS GAS COOLER OUTLET TO FINAL/INTERMEDIATE DISCHARGE HEADER | BIFFI | WGR3200 + ICON-020/180-144 (3000 Series) | 192273E007001 | Electrical | Not Available | Gb | IEC | Ex d. h ia | IIB | T4 | IP66/68 | -20 +85 | INE | IECEx INE 18.0026X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 647 | Ashik Kasim | 2023-07-24 06:00 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
648 | 42C2AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.61834,24.975223 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-118-ISO | 25-PC-108A | ISOLATOR, MOTOR OPERATED VALVE 25-MOV-118 | TECHNOR | CPSG-26/EFSRC-420 | 20P0092450012 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 648 | Ashik Kasim | 2023-07-24 06:09 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
649 | 492DAA4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6183297,24.9752278 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FZSC-102 | Not Available | Limit switch -Close- FCV-102 | Go switch | 22-11529-00M | 220902101612 | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T6 | IP66/68 | -40 +60 | Baseefa | Baseefa 12ATEX0160X | Yes | Others | Periodic | d | Close | A6. Circuit id not available | A6. Fix circuit id |  | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 649 | Ashik Kasim | 2023-07-24 06:23 | A6. Pending | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable
650 | 50C1AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6183375,24.9752468 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FZSO-102 | Not Available | Limit switch -Open FCV-102 | Go switch | 22-11529-00M | 220902101725 | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T6 | IP66/68 | -40 +60 | Baseefa | Baseefa 12ATEX0160X | Yes | Others | Periodic | d | Close | A6. Circuit id not available | A6. Fix circuit id |  | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 650 | Ashik Kasim | 2023-07-24 06:26 | A6. Pending | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable
651 | AABFAB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6182626,24.9752126 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FZSC-103 | Not Available | Limit switch -Close- FCV-103 | Go switch | 22-11529-00M | 220902101750 | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T6 | IP66/68 | -40 +60 | Baseefa | Baseefa 12ATEX0160X | Yes | Others | Periodic | d | Close | A6. Circuit id not available | A6. Fix circuit id |  | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 651 | Ashik Kasim | 2023-07-24 06:29 | A6. Pending | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable
652 | BCBEAB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6183026,24.9752001 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FZSO-103 | Not Available | Limit switch -Open FCV-103 | Go switch | 22-11529-00M | 220902101521 | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T6 | IP66/68 | -40 +60 | Baseefa | Baseefa 12ATEX0160X | Yes | Others | Periodic | d | Close | A6. Circuit id not available | A6. Fix circuit id |  | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 652 | Ashik Kasim | 2023-07-24 06:33 | A6. Pending | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable
653 | D3C5AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6182283,24.9750279 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2516T | CA_25-AE-2516T | FLAMMABLE GAS DETECTOR - OPEN PATH TYPE TRANSMITTER | Eye Safe | Quasar 900 | Not available | Instrumentation | Not Available | Gb | IEC | Ex db eb ib | Not stated | T4 | Not Visible | -55 +50 | Sira | IECEx SIR 13.0069X | Yes | Others | Periodic | d | Close | A10. Wrong type blanking elements installed | A10. Replace with suitable type blanking elements | Requires maintenance support to complete repair job | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 653 | Ashik Kasim | 2023-07-24 08:26 | A10. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding
654 | 30C1AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6183157,24.9750353 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-106 | CD_25-XY-106 | SOLENOID VALVE, SHUTDOWN VALVE OUTLET MEC-1 (25-C-101/102) | Bifold | FP06P-77A | FL10919-0377 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 654 | Ashik Kasim | 2023-07-24 08:32 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
655 | 6BC1AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6182352,24.9749941 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZSO-106/25-ZSC-106 | CD_25-ZS-106 | POSITION SWITCH , SHUTDOWN VALVE OUTLET MEC-1 (25-C-101/102) | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 655 | Ashik Kasim | 2023-07-24 08:40 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
656 | 4FBEAB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6182939,24.975088 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-2506 | CD_25-XY-2506 | SOLENOID VALVE, SHUTDOWN VALVE MEC INTERCONNECTION HEADER | Bifold | FP06P-77A | FL10919-0391 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 656 | Ashik Kasim | 2023-07-24 08:54 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
657 | 9AC0AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6182862,24.9751368 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZSO-2506/25-ZSC-2506 | CD_25-ZS-2506 | POSITION SWITCH OPEN, SHUTDOWN VALVE MEC INTERCONNECTION HEADER | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 657 | Ashik Kasim | 2023-07-24 09:04 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
658 | 19C5AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6182517,24.9751092 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-106 | CA_25-TIT-106 | TEMPERATURE TRANSMITTER, HP DISCHARGE GAS COOLER | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 3587949 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 658 | Ashik Kasim | 2023-07-24 09:12 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
659 | C1C1AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6182962,24.9751548 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FZT-102 | CA_FY/FZT-102 | POSITION TRANSMITTER, ANTI-SURGE CONTROL VALVE 25-C-102 -SERIES MODE | STI | Not Available | P-1901613 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -40 +60 | Baseefa | Baseefa 11ATEX0158X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 659 | Ashik Kasim | 2023-07-24 09:35 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
660 | 94BEAB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6183209,24.9751822 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | Not Available | CD_25-ZS-102 | Junction Box -FCV-102 | Pepperl+Fuchs | ES2315-0V | P221-256-03 | Instrumentation | 2 | Gb | IEC | Ex e | IIC | T6 | IP66 | -20 +55 | Sira | Sira09ATEX3135X | Yes | Others | Periodic | d | Close | A6. Equipment id not available | A6. Fix equipment id |  | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 660 | Ashik Kasim | 2023-07-24 09:46 | A6. Pending | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable
661 | 74BEAB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6183196,24.9752267 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FZT-103 | CA_FY/FZT-103 | POSITION TRANSMITTER, ANTI-SURGE CONTROL VALVE 25-C-103 -SERIES MODE | STI | Not Available | P-1901609 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -40 +60 | Baseefa | Baseefa 11ATEX0158X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 661 | Ashik Kasim | 2023-07-24 09:50 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
662 | B9C0AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6183539,24.9752363 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | Not Available | CD_25-ZS-103 | Junction Box -FCV-103 | Pepperl+Fuchs | ES2315-0V | P221-256-06 | Instrumentation | 2 | Gb | IEC | Ex e | IIC | T6 | IP66 | -20 +55 | Sira | Sira09ATEX3135X | Yes | Others | Periodic | d | Close | A6. Equipment id not available | A6. Fix equipment id |  | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 662 | Ashik Kasim | 2023-07-24 09:52 | A6. Pending | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable
663 | ECC3AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6182914,24.9752656 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-102 | CD_25-XY-102 | Solenoid Valve -25-FV-102 | ASCO | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex d | IIC | T5 | IP66/67 | -40 +70 | LCIE | LCIE00ATEX6008X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 663 | Ashik Kasim | 2023-07-24 10:06 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
664 | CABFAB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6182961,24.9752169 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-103 | CD_25-XY-103 | Solenoid Valve -25-FV-103 | ASCO | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex d | IIC | T5 | IP66/67 | -40 +70 | LCIE | LCIE00ATEX6008X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 664 | Ashik Kasim | 2023-07-24 10:08 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
665 | 27C2AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6183375,24.9752595 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2516R | CA_25-AE-2516R | FLAMMABLE GAS DETECTOR - OPEN PATH TYPE TRANSMITTER | Eye Safe | Quasar 900 | Not available | Instrumentation | Not Available | Gb | IEC | Ex db eb ib | Not stated | T4 | Not Visible | -55 +50 | Sira | 00ATEX1182X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 665 | Ashik Kasim | 2023-07-24 10:19 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
666 | BCC1AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6182058,24.9751434 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PDIT-2513 | CA_25-PDIT-2513 | DP TRANSMITTER, 25-XV-2563 | Rosemount | 300S1AAD1E7M5 | 942303 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T5 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 666 | Ashik Kasim | 2023-07-24 10:25 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
667 | EEC1AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler (+15) | 55.6183282,24.9751085 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PDIT-2514 | CA_25-PDIT-2514 | DP TRANSMITTER, 25-XV-2564 | Rosemount | 300S1AAD1E7M5 | 942304 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T5 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 667 | Ashik Kasim | 2023-07-24 10:30 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
668 | 78BEAB4E080104E0 |  | Margham | Area 25 | MEC 02 Pipeline Area-Ground | 55.6182446,24.9749296 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-UJBS-2522 | CA_25-UjBS-2522-01 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039881 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 668 | Ashik Kasim | 2023-07-24 10:36 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
669 | 44C0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Pipeline Area-Ground | 55.6182459,24.974926 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-UJBD-2523 | CD_25-UJBD-2523 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039941 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 669 | Ashik Kasim | 2023-07-24 10:40 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
670 | 275BAB4E080104E0 |  | Margham | Area 25 | MEC 02 Pipeline Area-Ground | 55.618215,24.9749519 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-UJBS-2524 | CD_25-UJBD-2524-01 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039914 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 670 | Ashik Kasim | 2023-07-24 10:43 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
671 | D92CAA4E080104E0 |  | Margham | Area 25 | MEC 02 Pipeline Area-Ground | 55.618256,24.9748903 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-DJBS-2522 | CD_25-DJBS-2522 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-03895 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 671 | Ashik Kasim | 2023-07-24 10:45 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
672 | 8FC2AB4E080104E0 |  | Margham | Area 25 | MEC 02 Pipeline Area-Ground | 55.618256,24.9748903 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FJBS-2522 | CD_25-FJBS-2522 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039922 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 672 | Ashik Kasim | 2023-07-24 10:49 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
673 | B8C1AB4E080104E0 |  | Margham | Area 25 | MEC 02 Pipeline Area-Ground | 55.6182186,24.9748684 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-DJBD-2523 | CD_25-DJBD-2523 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039937 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 673 | Ashik Kasim | 2023-07-25 05:46 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
674 | 99BFAB4E080104E0 |  | Margham | Area 25 | MEC 02 Pipeline Area-Ground | 55.6182561,24.9749092 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-DJBD-2524 | CD_25-DJBD-2524 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039928 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 674 | Ashik Kasim | 2023-07-25 05:49 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
675 | 2EC3AB4E080104E0 |  | Margham | Area 25 | MEC 02 Pipeline Area-Ground | 55.6182612,24.9748409 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-UJBD-2525 | CD_25-UJBD-2525 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039891 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 675 | Ashik Kasim | 2023-07-25 05:53 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
676 | A7BFAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6184115,24.9747436 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LCS-202A | 25-CC-107 | LCS - HP DISCHARGE COOLER MOTOR, 25-M-202C | BARTEC | 19D1009s/01 | 3937544-10-25 | Electrical | 2 | Gb | IEC | Ex db | IIB+H2 | T6 | IP66 | -5 +58 | DEKRA | DEKRA 13ATEX0209 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 676 | Ashik Kasim | 2023-07-25 05:59 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
677 | 2AC1AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6184732,24.9747739 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LCS-202B | 25-CC-104 | LCS - HP DISCHARGE COOLER MOTOR, 25-M-202B | BARTEC | 19D1009s/01 | 3937544-10-01 | Electrical | 2 | Gb | IEC | Ex db | IIB+H2 | T6 | IP66 | -5 +58 | DEKRA | DEKRA 13ATEX0209 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 677 | Ashik Kasim | 2023-07-25 06:02 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
678 | FFC1AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6184677,24.9747672 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LCS-202A | 25-CC-101 | LCS - HP DISCHARGE COOLER MOTOR, 25-M-202A | BARTEC | 19D1009s/01 | 3937544-10-23 | Electrical | 2 | Gb | IEC | Ex db | IIB+H2 | T6 | IP66 | -5 +58 | DEKRA | DEKRA 13ATEX0209 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 678 | Ashik Kasim | 2023-07-25 06:06 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
679 | C2C0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6184547,24.9748907 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LCS-201F | 25-CC-098 | LCS - LP DISCHARGE COOLER MOTOR, 25-M-201F | BARTEC | 19D1009s/01 | 3937544-10-22 | Electrical | 2 | Gb | IEC | Ex db | IIB+H2 | T6 | IP66 | -5 +58 | DEKRA | DEKRA 13ATEX0209 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 679 | Ashik Kasim | 2023-07-25 06:14 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
680 | 8EBFAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6184546,24.9749199 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LCS-201D | 25-CC-092 | LCS - LP DISCHARGE COOLER MOTOR, 25-M-201D | BARTEC | 19D1009s/01 | 3937544-10-06 | Electrical | 2 | Gb | IEC | Ex db | IIB+H2 | T6 | IP66 | -5 +58 | DEKRA | DEKRA 13ATEX0209 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 680 | Ashik Kasim | 2023-07-25 06:16 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
681 | 5DC1AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6184853,24.9750222 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LCS-201B | 25-CC-086 | LCS - LP DISCHARGE COOLER MOTOR, 25-M-201B | BARTEC | 19D1009s/01 | 3937544-10-10 | Electrical | 2 | Gb | IEC | Ex db | IIB+H2 | T6 | IP66 | -5 +58 | DEKRA | DEKRA 13ATEX0209 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 681 | Ashik Kasim | 2023-07-25 06:19 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
682 | B5C1AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6184693,24.9750842 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LCS-201E | 25-CC-095 | LCS - LP DISCHARGE COOLER MOTOR, 25-M-201E | BARTEC | 19D1009s/01 | 3937544-10-08 | Electrical | 2 | Gb | IEC | Ex db | IIB+H2 | T6 | IP66 | -5 +58 | DEKRA | DEKRA 13ATEX0209 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 682 | Ashik Kasim | 2023-07-25 06:23 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
683 | 0CC2AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6184607,24.975099 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LCS-201C | 25-CC-089 | LCS - LP DISCHARGE COOLER MOTOR, 25-M-201C | BARTEC | 19D1009s/01 | 3937544-10-18 | Electrical | 2 | Gb | IEC | Ex db | IIB+H2 | T6 | IP66 | -5 +58 | DEKRA | DEKRA 13ATEX0209 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 683 | Ashik Kasim | 2023-07-25 06:27 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
684 | 90C2AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6184268,24.9749324 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LCS-201A | 25-CC-083 | LCS - LP DISCHARGE COOLER MOTOR, 25-M-201A | BARTEC | 19D1009s/01 | 3937544-10-19 | Electrical | 2 | Gb | IEC | Ex db | IIB+H2 | T6 | IP66 | -5 +58 | DEKRA | DEKRA 13ATEX0209 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 684 | Ashik Kasim | 2023-07-25 06:29 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
685 | DEC5AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183582,24.9750656 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2546 | Not Available | TRIPLE IR FLAME DETECTOR | Rosemount | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T4 | IP68 | -60 +85 | Sira | Sira15ATEX1364X | Yes | Others | Periodic | d | Close | A10. Wrong type blanking elements installed | A10. Replace with suitable type blanking elements |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 685 | Ashik Kasim | 2023-07-25 08:26 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-08-18 08:29
686 | AAC5AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+30)Top | 55.6183593,24.9751764 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2545 | Not Available | TRIPLE IR FLAME DETECTOR | Rosemount | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T4 | IP68 | -60 +85 | Sira | Sira15ATEX1364X | Yes | Others | Periodic | d | Close | A10. Wrong type blanking elements installed | A10. Replace with suitable type blanking elements |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 686 | Ashik Kasim | 2023-07-25 08:37 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-08-18 08:38
687 | 0BC0AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6185714,24.9751187 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-101F | 25-PC-062A | MOTOR, LP DISCHARGE COOLER, 25-E-101B | ABB | 3GGP222220-AOL+VC | 3G1F1915583201 | Electrical | 3 | Gc | IEC | Ex ec | IIC | T3 | IP65 | -20 +60 | DEMKO | DEMKO18ATEX2076X | Yes | Motor | Initial | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 687 | Ashik Kasim | 2023-07-25 09:02 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
688 | 53C0AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6185714,24.9751387 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XSSH-101F | CD_25-XSSH-101F | VIBROSWITCH, MOTOR, LP DISCHARGE COOLER, 25-E-101B | METRIC | 5550-421-041 | Not Available | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 688 | Ashik Kasim | 2023-07-25 09:12 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
689 | E3C0AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6184577,24.9750826 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-101D | 25-PC-058 | MOTOR, LP DISCHARGE COOLER, 25-E-101B | ABB | 3GGP222220-AOL+VC | 3G1F1915583199 | Electrical | 3 | Gc | IEC | Ex ec | IIC | T3 | IP65 | -20 +60 | DEMKO | DEMKO18ATEX2076X | Yes | Motor | Initial | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 689 | Ashik Kasim | 2023-07-25 09:17 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
690 | 79BEAB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6184769,24.9751602 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XSSH-101D | CD_25-XSSH-101D | VIBROSWITCH, MOTOR, LP DISCHARGE COOLER, 25-E-101B | METRIC | 5550-421-041 | Not Available | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 690 | Ashik Kasim | 2023-07-25 09:20 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
691 | 43C0AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6184668,24.9750982 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-101B | 25-PC-054 | MOTOR, LP DISCHARGE COOLER, 25-E-101B | ABB | 3GGP222220-AOL+VC | 3G1F1915583197 | Electrical | 3 | Gc | IEC | Ex ec | IIC | T3 | IP65 | -20 +60 | DEMKO | DEMKO18ATEX2076X | Yes | Motor | Initial | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 691 | Ashik Kasim | 2023-07-25 09:27 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
692 | A0C0AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6184106,24.9751424 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XSSH-101B | CD_25-XSSH-101B | VIBROSWITCH, MOTOR, LP DISCHARGE COOLER, 25-E-101B | METRIC | 5550-421-041 | Not Available | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 692 | Ashik Kasim | 2023-07-25 09:31 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
693 | 1CC1AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6184898,24.9752185 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-101E | 25-PC-060A | MOTOR, LP DISCHARGE COOLER, 25-E-101A | ABB | 3GGP222220-AOL+VC | 3G1F1915583200 | Electrical | 3 | Gc | IEC | Ex ec | IIC | T3 | IP65 | -20 +60 | DEMKO | DEMKO18ATEX2076X | Yes | Motor | Initial | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 693 | Ashik Kasim | 2023-07-25 09:40 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
694 | B6C1AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6184854,24.9752735 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XSSH-101E | CD_25-XSSH-101B | VIBROSWITCH, MOTOR, LP DISCHARGE COOLER, 25-E-101A | METRIC | 5550-421-041 | Not Available | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 694 | Ashik Kasim | 2023-07-25 09:42 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
695 | 7AC1AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6185947,24.9753383 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-101C | 25-PC-056A | MOTOR, LP DISCHARGE COOLER, 25-E-101A | ABB | 3GGP222220-AOL+VC | 3G1F1915583198 | Electrical | 3 | Gc | IEC | Ex ec | IIC | T3 | IP65 | -20 +60 | DEMKO | DEMKO18ATEX2076X | Yes | Motor | Initial | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 695 | Ashik Kasim | 2023-07-25 09:54 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
696 | 45C0AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6184906,24.9752624 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XSSH-101C | CD_25-XSSH-101C | VIBROSWITCH, MOTOR, LP DISCHARGE COOLER, 25-E-101A | METRIC | 5550-421-041 | Not Available | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 696 | Ashik Kasim | 2023-07-25 10:02 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
697 | A0BEAB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6184634,24.975266 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-101A | 25-PC-052A | MOTOR, LP DISCHARGE COOLER, 25-E-101A | ABB | 3GGP222220-AOL+VC | 3G1F1915583196 | Electrical | 3 | Gc | IEC | Ex ec | IIC | T3 | IP65 | -20 +60 | DEMKO | DEMKO18ATEX2076X | Yes | Motor | Initial | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 697 | Ashik Kasim | 2023-07-25 10:09 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
698 | 27C4AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6184009,24.9751489 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XSSH-101A | CD_25-XSSH-101A | VIBROSWITCH, MOTOR, LP DISCHARGE COOLER, 25-E-101A | METRIC | 5550-421-041 | Not Available | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 698 | Ashik Kasim | 2023-07-25 10:12 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
699 | F7C3AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6183175,24.9751195 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-102A | 25-PC-064 | MOTOR, HP DISCHARGE COOLER, 25-E-102 | ABB | 3GGP222220-AOL+VC | 3G1F1915583186 | Electrical | 3 | Gc | IEC | Ex ec | IIC | T3 | IP65 | -20 +60 | DEMKO | DEMKO18ATEX2076X | Yes | Motor | Initial | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 699 | Ashik Kasim | 2023-07-25 10:17 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
700 | E9C4AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6183269,24.9750549 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XSSH-102A | CD_25-XSSH-102A | VIBROSWITCH, MOTOR, HP DISCHARGE COOLER, 25-E-102 | METRIC | 5550-421-041 | Not Available | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 700 | Ashik Kasim | 2023-07-25 10:22 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
701 | 86C4AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6184326,24.97507 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-102B | 25-PC-066 | MOTOR, HP DISCHARGE COOLER, 25-E-102 | ABB | 3GGP222220-AOL+VC | 3G1F1915583187 | Electrical | 3 | Gc | IEC | Ex ec | IIC | T3 | IP65 | -20 +60 | DEMKO | DEMKO18ATEX2076X | Yes | Motor | Initial | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 701 | Ashik Kasim | 2023-07-25 10:25 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
702 | 32C0AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6184627,24.9750375 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XSSH-102B | CD_25-XSSH-102B | VIBROSWITCH, MOTOR, HP DISCHARGE COOLER, 25-E-102 | METRIC | 5550-421-041 | Not Available | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 702 | Ashik Kasim | 2023-07-25 10:28 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
703 | D0C1AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.6185422,24.975061 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-102C | 25-PC-068 | MOTOR, HP DISCHARGE COOLER, 25-E-102 | ABB | 3GGP222220-AOL+VC | 3G1F1915583186 | Electrical | 3 | Gc | IEC | Ex ec | IIC | T3 | IP65 | -20 +60 | DEMKO | DEMKO18ATEX2076X | Yes | Motor | Initial | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 703 | Ashik Kasim | 2023-07-25 10:31 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
704 | 0EC2AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler Fan Deck (+15) | 55.618697,24.9750543 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XSSH-102C | CD_25-XSSH-102C | VIBROSWITCH, MOTOR, HP DISCHARGE COOLER, 25-E-102 | METRIC | 5550-421-041 | Not Available | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 704 | Ashik Kasim | 2023-07-25 10:33 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
705 | 10C2AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6185033,24.9747541 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-202C | 25-PC-087A | ISOLATOR, MOTOR 25-M-202C | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440028 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 705 | Ashik Kasim | 2023-07-26 05:39 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
706 | 81C4AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6184336,24.97469 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-202B | 25-PC-085A | ISOLATOR, MOTOR 25-M-202B | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440013 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 706 | Ashik Kasim | 2023-07-26 05:41 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
707 | 10C0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6183997,24.9747863 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-202A | 25-PC-083A | ISOLATOR, MOTOR 25-M-202A | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440008 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 707 | Ashik Kasim | 2023-07-26 05:45 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
708 | 9EC0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.61848,24.9748757 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-201F | 25-PC-081A | ISOLATOR, MOTOR 25-M-201A | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440015 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 708 | Ashik Kasim | 2023-07-26 05:48 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
709 | 975CAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6184269,24.9749593 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-201D | 25-PC-077A | ISOLATOR, MOTOR 25-M-201D | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440003 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 709 | Ashik Kasim | 2023-07-26 05:50 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
710 | C45AAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6184332,24.9749204 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-201B | 25-PC-073A | ISOLATOR, MOTOR 25-M-201B | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440026 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 710 | Ashik Kasim | 2023-07-26 05:52 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
711 | B3BEAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6184183,24.9750984 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-201E | 25-PC-079A | ISOLATOR, MOTOR 25-M-201E | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440030 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 711 | Ashik Kasim | 2023-07-26 05:57 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
712 | 28C2AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6184233,24.9750636 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-201C | 25-PC-075B | ISOLATOR, MOTOR 25-M-201C | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440018 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close | A10. Loose bolts A15. Flange joint gaps exceeded permitted value | A10. Tighten bolts A15. Repair equipment by maintaining the IP |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 712 | Ashik Kasim | 2023-07-26 06:04 | A10. Done A15. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Not Applicable | Ashik Kasim | 2023-08-15 10:40
713 | B3BFAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6185007,24.9750292 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-201A | 25-PC-071A | ISOLATOR, MOTOR 25-M-201A | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440035 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 713 | Ashik Kasim | 2023-07-26 06:09 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
714 | F0C4AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6183369,24.9750743 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-VJBD-2521 | CD_25-VJBD-2521 | JUNCTION BOX FOR LP DISCHARGE COOLERS | STAHL | 8150/1-0200-0300-150-3321 | 1916661520440002 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T4 | IP66 | -60 +70 | PTB | PTB09ATEX1108 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 714 | Ashik Kasim | 2023-07-26 06:13 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
715 | 63C0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.618345,24.9746305 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-VJBD-2522 | CD_25-VJBD-2522 | JUNCTION BOX FOR HP DISCHARGE COOLERS | STAHL | 8150/1-0200-0300-150-3321 | Not Available | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T4 | IP66 | -60 +70 | PTB | PTB09ATEX1108 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 715 | Ashik Kasim | 2023-07-26 06:18 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
716 | 13C0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6184089,24.9749323 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FIT-200 | CA_25-FIT-200 | FLOW TRANSMITTER, AREA 25 COMPRESSOR B | Rosemount | 300S1AAD1E7M5 | 942624 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECExKEM08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 716 | Ashik Kasim | 2023-07-26 06:25 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
717 | B8C3AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6183681,24.9749203 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-200 | CA_25-PIT-200 | PRESSURE TRANSMITTER, AREA 25 COMPRESSOR B | Rosemount | 3051SAAD1E7M5 | 0942216 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECExKEM08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 717 | Ashik Kasim | 2023-07-26 06:28 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
718 | 015CAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6183682,24.9749791 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-200 | CA_25-TIT-100 | TEMPERATURE TRANSMITTER, AREA 25 COMPRESSOR B | Rosemount | 3144PD1A2E7B4M5CNC4Q4U1QTXAK1105 | 3587940 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECExFMG12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 718 | Ashik Kasim | 2023-07-26 06:31 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
719 | AAC1AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6182651,24.974961 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-205 | CA_25-TIT-205 | TEMPERATURE TRANSMITTER, LP DISCHARGE GAS COOLER | Rosemount | 3144PD1A2E7B4M5CNC4Q4U1QTXAK1105 | 3587964 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECExFMG12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 719 | Ashik Kasim | 2023-07-26 06:36 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
720 | FCC0AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6184975,24.9753005 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XA-2503G | CD_25-XA-2503G | SINGLE TONE SOUNDER (WITH ADJUSTABLE TONE & VOLUME) | EATON | DB3BG | 215685819 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T4 | Not Available | -55 +85 | Baseefa | Baseefa13ATEX0229X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 720 | Ashik Kasim | 2023-07-26 08:20 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
721 | A9BEAB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6185058,24.9753014 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XA-2503F | CD_25-XA-2503F | SINGLE TONE SOUNDER (WITH ADJUSTABLE TONE & VOLUME) | EATON | DB3BG | 215685819 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T4 | Not Available | -55 +85 | Baseefa | Baseefa13ATEX0229X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 721 | Ashik Kasim | 2023-07-26 08:23 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
722 | 89C1AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6185429,24.9753096 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XL-2503G | CD_25-XL-2503G | FLASHING BEACON (WITH RED GLASS FOR FIRE & BLUE GLASS FOR GAS) | EATON | XB4 | 2156958195103 | Instrumentation | Not Available | Gb | IEC | Ex d | IIC | T4 | IP65 | -55 +60 | BAS | IECExBAS10.0078X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 722 | Ashik Kasim | 2023-07-26 08:48 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
723 | F8C0AB4E080104E0 |  | Margham | Area 25 | MEC 01 Gas Cooler-Ground | 55.6185704,24.9753051 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XL-2503F | CD_25-XL-2503F | FLASHING BEACON (WITH RED GLASS FOR FIRE & BLUE GLASS FOR FIRE | EATON | XB4 | 2156958195103 | Instrumentation | Not Available | Gb | IEC | Ex d | IIC | T4 | IP65 | -55 +60 | BAS | IECExBAS10.0078X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 723 | Ashik Kasim | 2023-07-26 09:00 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
724 | A4BFAB4E080104E0 |  | Margham | Area 25 | MEC 01 GC Motor Cooler Area | 55.6181625,24.9752242 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-120A | 25-PC-008 | MOTOR, MEC 1 COOLING GAS AIR COOLER 1, 25-E-120A | WEG | W22XdBE | 24ABR20191048686429 | Electrical | 2 | Gb | IEC | Ex de | IIB | T4 | Not Available | -40 +60 | Baseefa | Baseefa13ATEX028X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 724 | Ashik Kasim | 2023-07-26 09:11 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
725 | 92BEAB4E080104E0 |  | Margham | Area 25 | MEC 01 GC Motor Cooler Area | 55.6181945,24.9751894 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-120B | 25-PC-010 | MOTOR, MEC 1 COOLING GAS AIR COOLER 1, 25-E-120B | WEG | W22XdBE | 24ABR20191048686430 | Electrical | 2 | Gb | IEC | Ex de | IIB | T4 | Not Available | -40 +60 | Baseefa | Baseefa13ATEX028X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 725 | Ashik Kasim | 2023-07-26 09:19 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
726 | B3C4AB4E080104E0 |  | Margham | Area 25 | MEC 01 GC Motor Cooler Area | 55.618202,24.975292 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-VSH-121 | CD_25-VSH-121 | VIBROSWITCH, MOTOR, MEC 1 COOLING GAS AIR COOLER 1, 25-E-120A | METRIC | 5550-421-040 | 778232 | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 726 | Ashik Kasim | 2023-07-26 09:26 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
727 | E6C0AB4E080104E0 |  | Margham | Area 25 | MEC 01 GC Motor Cooler Area | 55.6181799,24.975249 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-VSH-122 | CD_25-VSH-122 | VIBROSWITCH, MOTOR, MEC 1 COOLING GAS AIR COOLER 1, 25-E-120B | METRIC | 5550-421-040 | 778233 | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 727 | Ashik Kasim | 2023-07-26 09:30 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
728 | 71BEAB4E080104E0 |  | Margham | Area 25 | MEC 01 GC Motor Cooler Area | 55.6180213,24.9751869 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2517 | CA_25-AE-2517 | FLAMMABLE GAS DETECTOR - IR POINT TYPE | Net Safety | SC311S-100-ASSY | 085905 | Instrumentation | Not Available | Gb | IEC | Ex d | IIB + H2 | T5 | IP64 | -40 +75 | FMG | IECExFMG 12.0007X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 728 | Ashik Kasim | 2023-07-26 09:52 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
729 | 2FC3AB4E080104E0 |  | Margham | Area 25 | MEC 01 GC Motor Cooler Area | 55.6180979,24.975262 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2513 | CA_25-AE-2513 | FLAMMABLE GAS DETECTOR - IR POINT TYPE | Net Safety | SC311S-100-ASSY | 085903 | Instrumentation | Not Available | Gb | IEC | Ex d | IIB + H2 | T5 | IP64 | -40 +75 | FMG | IECExFMG 12.0007X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 729 | Ashik Kasim | 2023-07-26 09:54 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
730 | 69C2AB4E080104E0 |  | Margham | Area 25 | MEC 01 GC Motor Cooler Area | 55.6181861,24.9752196 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-120A | 25-PC-009A | ISOLATOR, MOTOR 25-M-120A | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440021 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 730 | Ashik Kasim | 2023-07-26 09:59 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
731 | 04C1AB4E080104E0 |  | Margham | Area 25 | MEC 01 GC Motor Cooler Area | 55.618123,24.9751699 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-120B | 25-PC-011A | ISOLATOR, MOTOR 25-M-120B | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440019 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 731 | Ashik Kasim | 2023-07-26 10:02 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
732 | ECC1AB4E080104E0 |  | Margham | Area 25 | MEC 01 GC Motor Cooler Area | 55.6181993,24.9751657 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 27-JB-127 | CD_25-E120A/B | Junction Box | Technor | SB-273516 | I/19/20941 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T6 | Not Available | -20 +60 | IMQ | IECEx IMQ 15.0002X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 732 | Ashik Kasim | 2023-07-26 10:09 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
733 | 1DC2AB4E080104E0 |  | Margham | Area 25 | MEC 01 GC Motor Cooler Area | 55.6178821,24.9752406 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HS-121C | CD_25-HS-121C | Exd Hand Switch -M-120-A | Cortem Group | EFSCO-64 | 19/343216 | Electrical | 2 | Gb | IEC | Ex db | IIC | T5 | IP66 | -20 +55 | CESI | CESI01ATEX092X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 733 | Ashik Kasim | 2023-07-26 10:20 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
734 | 88C3AB4E080104E0 |  | Margham | Area 25 | MEC 01 GC Motor Cooler Area | 55.6181876,24.9752799 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HS-122C | CD_25-HS-122C | Exd Hand Switch -M-120-B | Cortem Group | EFSCO-64 | 19/343217 | Electrical | 2 | Gb | IEC | Ex db | IIC | T5 | IP66 | -20 +55 | CESI | CESI01ATEX092X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 734 | Ashik Kasim | 2023-07-26 10:38 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
735 | 7EC1AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6186604,24.9749347 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-202C | 25-PC-087B | MOTOR, HP DISCHARGE COOLER, 25-E-202 | ABB | 3GGP222220-AOL+VC | 3G1F1915583191 | Electrical | 3 | Gc | IEC | Ex ec | IIC | T3 | IP65 | -20 +60 | DEMKO | DEMKO18ATEX2076X | Yes | Motor | Initial | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 735 | Ashik Kasim | 2023-07-27 05:42 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
736 | DFC5AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6186452,24.9747846 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XSSH-202C | CD_25-XSSH-202C | VIBROSWITCH, MOTOR, LP DISCHARGE COOLER, 25-E-202C | METRIC | 5550-421-041 | 780260 | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 736 | Ashik Kasim | 2023-07-27 05:47 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
737 | 95BFAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.618493,24.9747115 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-202B | 25-PC-084 | MOTOR, HP DISCHARGE COOLER, 25-E-202 | ABB | 3GGP222220-AOL+VC | 3G1F1915583190 | Electrical | 3 | Gc | IEC | Ex ec | IIC | T3 | IP65 | -20 +60 | DEMKO | DEMKO18ATEX2076X | Yes | Motor | Initial | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 737 | Ashik Kasim | 2023-07-27 05:53 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
738 | F6C2AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6184794,24.9747135 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XSSH-202B | CD_25-XSSH-202B | VIBROSWITCH, MOTOR, LP DISCHARGE COOLER, 25-E-202C | METRIC | 5550-421-041 | 780257 | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 738 | Ashik Kasim | 2023-07-27 05:55 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
739 | F1C2AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6184248,24.9746984 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-202A | 25-PC-082 | MOTOR, HP DISCHARGE COOLER, 25-E-202 | ABB | 3GGP222220-AOL+VC | 3G1F1915583189 | Electrical | 3 | Gc | IEC | Ex ec | IIC | T3 | IP65 | -20 +60 | DEMKO | DEMKO18ATEX2076X | Yes | Motor | Initial | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 739 | Ashik Kasim | 2023-07-27 05:58 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
740 | 9FBFAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.61837,24.9747072 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XSSH-202A | CD_25-XSSH-202A | VIBROSWITCH, MOTOR, LP DISCHARGE COOLER, 25-E-202C | METRIC | 5550-421-041 | 780264 | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 740 | Ashik Kasim | 2023-07-27 06:01 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
741 | 0EC6AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6185192,24.9747887 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-201F | 25-PC-080A | MOTOR, LP DISCHARGE COOLER, 25-E-201B | ABB | 3GGP222220-AOL+VC | 3G1F1915583336 | Electrical | 3 | Gc | IEC | Ex ec | IIC | T3 | IP65 | -20 +60 | DEMKO | DEMKO18ATEX2076X | Yes | Motor | Initial | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 741 | Ashik Kasim | 2023-07-27 06:07 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
742 | 27C3AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6185314,24.9747976 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XSSH-201F | CD_25-XSSH-201F | VIBROSWITCH, MOTOR, LP DISCHARGE COOLER, 25-E-201B | METRIC | 5550-421-041 | 780264 | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 742 | Ashik Kasim | 2023-07-27 06:09 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
743 | 22C0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6184854,24.9748508 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-201D | 25-PC-076A | MOTOR, LP DISCHARGE COOLER, 25-E-201B | ABB | 3GGP222220-AOL+VC | 3G1F1915583205 | Electrical | 3 | Gc | IEC | Ex ec | IIC | T3 | IP65 | -20 +60 | DEMKO | DEMKO18ATEX2076X | Yes | Motor | Initial | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 743 | Ashik Kasim | 2023-07-27 06:12 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
744 | FCBFAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6184804,24.9748705 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XSSH-201D | CD_25-XSSH-201D | VIBROSWITCH, MOTOR, LP DISCHARGE COOLER, 25-E-201B | METRIC | 5550-421-041 | 780256 | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 744 | Ashik Kasim | 2023-07-27 06:16 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
745 | 6CC0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6183722,24.9747464 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-201B | 25-PC-072A | MOTOR, LP DISCHARGE COOLER, 25-E-201B | ABB | 3GGP222220-AOL+VC | 3G1F1915583203 | Electrical | 3 | Gc | IEC | Ex ec | IIC | T3 | IP65 | -20 +60 | DEMKO | DEMKO18ATEX2076X | Yes | Motor | Initial | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 745 | Ashik Kasim | 2023-07-27 06:20 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
746 | AFBEAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6183971,24.9748333 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XSSH-201B | CD_25-XSSH-201B | VIBROSWITCH, MOTOR, LP DISCHARGE COOLER, 25-E-201B | METRIC | 5550-421-041 | 780244 | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 746 | Ashik Kasim | 2023-07-27 06:23 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
747 | 93BFAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6185065,24.9747181 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-201E | 25-PC-078A | MOTOR, LP DISCHARGE COOLER, 25-E-201A | ABB | 3GGP222220-AOL+VC | 3G1F1915583335 | Electrical | 3 | Gc | IEC | Ex ec | IIC | T3 | IP65 | -20 +60 | DEMKO | DEMKO18ATEX2076X | Yes | Motor | Initial | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 747 | Ashik Kasim | 2023-07-27 06:28 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
748 | A2C0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6185193,24.9749342 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XSSH-201E | CD_25-XSSH-201E | VIBROSWITCH, MOTOR, LP DISCHARGE COOLER, 25-E-201A | METRIC | 5550-421-041 | 780269 | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 748 | Ashik Kasim | 2023-07-27 06:37 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
749 | 8DC4AB4E080104E0 |  | Margham | Area 25 | MEC 01 GC Motor Cooler Area | 55.6181671,24.9752694 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2543 | CA_25-AE-2543 | TRIPLE IR FLAME DETECTOR | Rosemount | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T4 | IP68 | -60 +85 | Sira | Sira15ATEX1364X | Yes | Others | Periodic | d | Close | A10. Wrong type blanking elements installed | A10. Replace with suitable type blanking elements | Teflon tape used | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 749 | Ashik Kasim | 2023-07-27 08:14 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-08-18 11:50
750 | 57C4AB4E080104E0 |  | Margham | Area 25 | MEC 01 GC Motor Cooler Area | 55.6181802,24.9752439 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2544 | CA_25-AE-2544 | TRIPLE IR FLAME DETECTOR | Rosemount | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T4 | IP68 | -60 +85 | Sira | Sira15ATEX1364X | Yes | Others | Periodic | d | Close | A10. Wrong type blanking elements installed | A10. Replace with suitable type blanking elements | Teflon tape used | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 750 | Ashik Kasim | 2023-07-27 08:22 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-08-18 11:27
751 | 62BEAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+30)Top | 55.6183158,24.9748032 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2556 | CA_25-AE-2556 | TRIPLE IR FLAME DETECTOR | Rosemount | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T4 | IP68 | -60 +85 | Sira | Sira15ATEX1364X | Yes | Others | Periodic | d | Close | A10. Wrong type blanking elements installed | A10. Replace with suitable type blanking elements | Teflon tape used | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 751 | Ashik Kasim | 2023-07-27 08:36 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-08-18 10:24
752 | F72CAA4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+30)Top | 55.6183792,24.9749328 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2555 | CA_25-AE-2555 | TRIPLE IR FLAME DETECTOR | Rosemount | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T4 | IP68 | -60 +85 | Sira | Sira15ATEX1364X | Yes | Others | Periodic | d | Close | A10. Wrong type blanking elements installed | A10. Replace with suitable type blanking elements | Teflon tape used | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 752 | Ashik Kasim | 2023-07-27 08:50 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-08-18 10:30
753 | 20C3AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6184535,24.9750001 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-201C | 25-PC-074A | MOTOR, LP DISCHARGE COOLER, 25-E-201A | ABB | 3GGP222220-AOL+VC | 3G1F1915583204 | Electrical | 3 | Gc | IEC | Ex ec | IIC | T3 | IP65 | -20 +60 | DEMKO | DEMKO18ATEX2076X | Yes | Motor | Initial | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 753 | Ashik Kasim | 2023-07-27 09:00 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
754 | 28C4AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6184455,24.9750043 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XSSH-201C | CD_25-XSSH-201C | VIBROSWITCH, MOTOR, LP DISCHARGE COOLER, 25-E-201A | METRIC | 5550-421-041 | 780267 | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 754 | Ashik Kasim | 2023-07-27 09:08 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
755 | 005BAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6184418,24.9750103 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-201A | 25-PC-070A | MOTOR, LP DISCHARGE COOLER, 25-E-201A | ABB | 3GGP222220-AOL+VC | 3G1F1915583202 | Electrical | 3 | Gc | IEC | Ex ec | IIC | T3 | IP65 | -20 +60 | DEMKO | DEMKO18ATEX2076X | Yes | Motor | Initial | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 755 | Ashik Kasim | 2023-07-27 09:10 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
756 | F9C0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler Fan Deck (+15) | 55.6184398,24.9749812 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XSSH-201A | CD_25-XSSH-201A | VIBROSWITCH, MOTOR, LP DISCHARGE COOLER, 25-E-201A | METRIC | 5550-421-041 | 780259 | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 756 | Ashik Kasim | 2023-07-27 09:14 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
757 | 15C1AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6182826,24.9747901 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-2524 | CD_25-MOV-2524 | MOV - 25-E-201/2 A/B OUTLET TO MEC INTERCONNECTION HEADER | BIFFI | WGR3200 + ICON-020/180-144 (3000 Series) | 192273E004001 | Electrical | Not Available | Gb | IEC | Ex d. h ia | IIB | T4 | IP66/68 | -20 +85 | INE | IECEx INE 18.0026X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 757 | Ashik Kasim | 2023-07-27 09:36 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
758 | BBC0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.618314,24.9748187 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-2524-ISO | 25-PC-122A | ISOLATOR, MOTOR OPERATED VALVE 25-MOV-2513 | TECHNOR | CPSG-26/EFSRC-420 | 20P0092450001 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 758 | Ashik Kasim | 2023-07-27 09:41 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
759 | 5F5AAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6183278,24.9748419 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZSC-2574/25-ZSO-2574 | CD_25-ZS-2574 | POSITION SWITCH , SHUTDOWN VALVE 25-MOV-2524 BYPASS LINE | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 759 | Ashik Kasim | 2023-07-27 09:45 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
760 | 0CC0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6182477,24.9748289 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-2574 | CD_25-XY-2574 | SOLENOID VALVE, SHUTDOWN VALVE 25-MOV-2524 BYPASS LINE | Bifold | FP06P-77A | FL10919-0362 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 760 | Ashik Kasim | 2023-07-27 09:49 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
761 | D2C0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6182813,24.974825 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZSO-2573/25-ZSC-2573 | CD_25-ZS-2573 | POSITION SWITCH , SHUTDOWN VALVE 25-MOV-2523 BYPASS LINE | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 761 | Ashik Kasim | 2023-07-27 09:53 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
762 | 0DC6AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6182928,24.9748177 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-2573 | CD_25-XY-2573 | SOLENOID VALVE, SHUTDOWN VALVE 25-MOV-2523 BYPASS LINE | Bifold | FP06P-77A | FL10919-0380 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 762 | Ashik Kasim | 2023-07-27 09:55 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
763 | E0BFAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.618342,24.9748123 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-2523 | CD_25-MOV-2523 | MOV - 25-E-201/2 A/B OUTLET TO MEC DISCHARGE HEADER | BIFFI | WGR3200 + ICON-020/180-144 (3000 Series) | 192273E005001 | Electrical | Not Available | Gb | IEC | Ex d. h ia | IIB | T4 | IP66/68 | -20 +85 | INE | IECEx INE 18.0026X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 763 | Ashik Kasim | 2023-07-27 10:02 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
764 | 15C0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6183312,24.9748266 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-2523-ISO | 25-PC-121A | ISOLATOR, MOTOR OPERATED VALVE 25-MOV-2523 | TECHNOR | CPSG-26/EFSRC-420 | 20P0092450002 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 764 | Ashik Kasim | 2023-07-27 10:06 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
765 | F2C4AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6183409,24.9749034 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZSO-208/25-ZSC-208 | CD_25-ZS-208 | POSITION SWITCH , BLOWDOWN VALVE PROCESS GAS COOLER OUTLET (25-E-202 A/B) | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 765 | Ashik Kasim | 2023-07-27 10:11 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
766 | 1CC5AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6182928,24.9748177 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-208 | CD_25-XY-208 | SOLENOID VALVE, BLOWDOWN VALVE PROCESS GAS COOLER OUTLET (25-E-202 A/B) | Bifold | FP06P-77A | FL10919-0365 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 766 | Ashik Kasim | 2023-07-27 10:19 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
767 | C6C1AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6182988,24.974932 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-218 | CD_25-MOV-218 | MOV - PROCESS GAS COOLER OUTLET TO FINAL/INTERMEDIATE DISCHARGE HEADER | BIFFI | WGR3200 + ICON-020/180-144 (3000 Series) | 192273E004001 | Electrical | Not Available | Gb | IEC | Ex d. h ia | IIB | T4 | IP66/68 | -20 +85 | INE | IECEx INE 18.0026X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 767 | Ashik Kasim | 2023-07-28 05:34 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
768 | D6C1AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6183366,24.9749487 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-218-ISO | 25-PC-111A | ISOLATOR, MOTOR OPERATED VALVE 25-MOV-218 | TECHNOR | CPSG-26/EFSRC-420 | 20P0092450002 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 768 | Ashik Kasim | 2023-07-28 05:36 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
769 | EDC4AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6183625,24.9749008 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FZT-203 | CA_FY/FZT-203 | POSITION TRANSMITTER, ANTI-SURGE CONTROL VALVE 25-C-202 - PARALLEL MODE | STI | Not Available | P-1901608 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -40 +60 | Baseefa | Baseefa 11ATEX0158X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 769 | Ashik Kasim | 2023-07-28 05:40 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
770 | D6BEAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6183157,24.9749539 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-203 | CD_25-XY-203 | Solenoid Valve -25-FV-203 | ASCO | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex d | IIC | T5 | IP66/67 | -40 +70 | LCIE | LCIE00ATEX6008X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 770 | Ashik Kasim | 2023-07-28 05:47 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
771 | C1C3AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6182913,24.9749454 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FZSC-203 | Not Available | Limit switch -Close- FCV-203 | Go switch | 22-11529-00M | 220906145843 | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T6 | IP66/68 | -40 +60 | Baseefa | Baseefa 12ATEX0160X | Yes | Others | Periodic | d | Close | A6. Circuit id not available | A6. Fix circuit id |  | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 771 | Ashik Kasim | 2023-07-28 05:51 | A6. Pending | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable
772 | 2AC3AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6183686,24.9749267 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FZSO-203 | Not Available | Limit switch -Open- FCV-203 | Go switch | 22-11529-00M | 220906101717 | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T6 | IP66/68 | -40 +60 | Baseefa | Baseefa 12ATEX0160X | Yes | Others | Periodic | d | Close | A6. Circuit id not available | A6. Fix circuit id |  | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 772 | Ashik Kasim | 2023-07-28 05:55 | A6. Pending | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable
773 | E25AAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6183111,24.9749041 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | Not Available | CD_25-ZS-203 | Junction Box -FCV-203 | Pepperl+Fuchs | ES2315-0V | P221-256-02 | Instrumentation | 2 | Gb | IEC | Ex e | IIC | T6 | IP66 | -20 +55 | Sira | Sira09ATEX3135X | Yes | Others | Periodic | d | Close | A6. Equipment id not available | A6. Fix equipment id |  | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 773 | Ashik Kasim | 2023-07-28 06:00 | A6. Pending | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable
774 | 3DC2AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6183776,24.9749252 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-202 | CD_25-XY-202 | Solenoid Valve -25-FV-202 | ASCO | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex d | IIC | T5 | IP66/67 | -40 +70 | LCIE | LCIE00ATEX6008X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 774 | Ashik Kasim | 2023-07-28 06:02 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
775 | 91C2AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6182909,24.9749198 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FZSC-202 | Not Available | Limit switch -Close- FCV-202 | Go switch | 22-11529-00M | 220829160839 | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T6 | IP66/68 | -40 +60 | Baseefa | Baseefa 12ATEX0160X | Yes | Others | Periodic | d | Close | A6. Circuit id not available | A6. Fix circuit id |  | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 775 | Ashik Kasim | 2023-07-28 06:05 | A6. Pending | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable
776 | 1FC1AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6182948,24.97493 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FZSO-202 | Not Available | Limit switch -Open- FCV-202 | Go switch | 22-11529-00M | 220902101511 | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T6 | IP66/68 | -40 +60 | Baseefa | Baseefa 12ATEX0160X | Yes | Others | Periodic | d | Close | A6. Circuit id not available | A6. Fix circuit id |  | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 776 | Ashik Kasim | 2023-07-28 06:09 | A6. Pending | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable
777 | 8DBFAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6183241,24.9749438 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | Not Available | CD_25-ZS-202 | Junction Box -FCV-202 | Pepperl+Fuchs | ES2315-0V | P221-256-01 | Instrumentation | 2 | Gb | IEC | Ex e | IIC | T6 | IP66 | -20 +55 | Sira | Sira09ATEX3135X | Yes | Others | Periodic | d | Close | A6. Equipment id not available | A6. Fix equipment id |  | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 777 | Ashik Kasim | 2023-07-28 06:11 | A6. Pending | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable
778 | CFC0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6183302,24.9749444 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FZT-202 | CA_FY/FZT-202 | POSITION TRANSMITTER, ANTI-SURGE CONTROL VALVE 25-C-101-SERIES MODE | STI | Not Available | P-1901612 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -40 +60 | Baseefa | Baseefa 11ATEX0158X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 778 | Ashik Kasim | 2023-07-28 06:15 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
779 | 21C4AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6183247,24.9749008 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-217 | CD_25-MOV-217 | MOV - PROCESS GAS COOLER OUTLET (25-E-201 A/B ) TO 25-C-202 | BIFFI | WGR3200 + ICON-020/180-144 (3000 Series) | 192273E005001 | Electrical | Not Available | Gb | IEC | Ex d. h ia | IIB | T4 | IP66/68 | -20 +85 | INE | IECEx INE 18.0026X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 779 | Ashik Kasim | 2023-07-28 06:18 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
780 | F6C3AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.618282,24.9748736 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-217-ISO | 25-PC-110A | ISOLATOR, MOTOR OPERATED VALVE 25-MOV-217 | TECHNOR | CPSG-26/EFSRC-420 | 20P0092450014 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 780 | Ashik Kasim | 2023-07-28 06:22 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
781 | A9C5AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6183074,24.9749231 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-206 | CA_25-TIT-206 | TEMPERATURE TRANSMITTER, HP DISCHARGE GAS COOLER | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 3587965 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 781 | Ashik Kasim | 2023-07-28 06:26 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
782 | DCBEAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6183639,24.9748475 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PDIT-2523 | CA_25-PDIT-2523 | DP TRANSMITTER, 25-XV-2573 | Rosemount | 300S1AAD1E7M5 | 942305 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T5 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 782 | Ashik Kasim | 2023-07-28 06:30 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
783 | 05C0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.618369,24.9748084 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PDIT-2524 | CA_25-PDIT-2524 | DP TRANSMITTER, 25-XV-2574 | Rosemount | 300S1AAD1E7M5 | 942306 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T5 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 783 | Ashik Kasim | 2023-07-28 06:35 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
784 | 0DC0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6179391,24.9751345 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-2508 | CA_25-PIT-2508 | PRESSURE TRANSMITTER, INSTRUMENT AIR SYSTEM | Rosemount | 300S1AAD1E7M5 | 0942178 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 784 | Ashik Kasim | 2023-07-28 08:16 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
785 | C2C3AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6181425,24.9747079 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2525R | CA_25-AE-2525R | FLAMMABLE GAS DETECTOR - OPEN PATH TYPE RECEIVER | Eye Safe | Quasar 900 | Not visible | Instrumentation | Not Applicable | Gb | IEC | Ex d | IIB + H2 | T4 | IP64 | -40 +75 | Sira | IECEx SIR 13.0069X | Yes | Others | Periodic | d | Close | A10. Wrong type blanking elements installed | A10. Replace with suitable type blanking elements | Teflon tape used along with Stop plugs | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 785 | Ashik Kasim | 2023-07-28 08:22 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-08-28 08:57
786 | A6BEAB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.618146,24.9747013 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PDIT-2521 | CA_25-PDIT-2521 | DP TRANSMITTER, 25-XV-2571 | Rosemount | 300S1AAD1E7M5 | 942293 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T5 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 786 | Ashik Kasim | 2023-07-28 08:30 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
787 | B4C4AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.618162,24.9747533 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-2571 | CD_25-XY-2571 | SOLENOID VALVE, SHUTDOWN VALVE 25-MOV-2521 BYPASS LINE | Bifold | FP06P-77A | FL10919-0870 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 787 | Ashik Kasim | 2023-07-28 08:34 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
788 | 6EBEAB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6182101,24.974755 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZSO-2571/25-ZSC-2571 | CD_25-ZS-2571 | POSITION SWITCH, SHUTDOWN VALVE 25-MOV-2521 BYPASS LINE | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 788 | Ashik Kasim | 2023-07-28 08:39 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
789 | 37C6AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6182256,24.9747446 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PDIT-200 | CA_25-PDIT-200 | DP TRANSMITTER, 25-XV-2571 | Rosemount | 300S1AAD1E7M5 | 942297 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T5 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 789 | Ashik Kasim | 2023-07-28 08:45 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
790 | 37C1AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6180976,24.974753 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-201 | CD_25-XY-201 | SOLENOID VALVE, EQUALIZING VALVE ACROSS 25-XV-200 | Bifold | FP06P-77A | FL10919-0367 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 790 | Ashik Kasim | 2023-07-28 08:56 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
791 | 53C4AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6181007,24.9747309 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZSO-201/25-ZSC-201 | CD_25-ZS-201 | POSITION SWITCH, EQUALIZING VALVE ACROSS 25-XV-200 | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 791 | Ashik Kasim | 2023-07-28 09:00 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
792 | 3C59AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6181464,24.9747535 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-2522 | CD_25-MOV-2522 | MOV - HP SUCTION HEADER-COMMON TO MEC 2 | BIFFI | WGR3200 + ICON-020/180-144 (3000 Series) | 192273E006001 | Electrical | Not Available | Gb | IEC | Ex d. h ia | IIB | T4 | IP66/68 | -20 +85 | INE | IECEx INE 18.0026X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 792 | Ashik Kasim | 2023-07-28 09:09 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
793 | D3BEAB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6181492,24.9748054 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-2522-ISO | 25-PC-120A | ISOLATOR, MOTOR OPERATED VALVE 25-MOV-2522 | TECHNOR | CPSG-26/EFSRC-420 | 20P0092450007 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 793 | Ashik Kasim | 2023-07-28 09:27 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
794 | 9BC2AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6181387,24.9747707 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-2521 | CD_25-MOV-2521 | MOV - LP SUCTION HEADER - COMMON TO MEC 2 | BIFFI | WGR3200 + ICON-020/180-144 (3000 Series) | 192273E007001 | Electrical | Not Available | Gb | IEC | Ex d. h ia | IIB | T4 | IP66/68 | -20 +85 | INE | IECEx INE 18.0026X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 794 | Ashik Kasim | 2023-07-28 09:22 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
795 | 2B2EAA4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6181065,24.9748017 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-2521-ISO | 25-PC-119A | ISOLATOR, MOTOR OPERATED VALVE 25-MOV-2521 | TECHNOR | CPSG-26/EFSRC-420 | 20P0092450023 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 795 | Ashik Kasim | 2023-07-28 09:36 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
796 | 52C0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6181443,24.9748441 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-2572 | CD_25-XY-2572 | SOLENOID VALVE, SHUTDOWN VALVE 25-MOV-2522 BYPASS LINE | Bifold | FP06P-77A | FL10919-0382 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 796 | Ashik Kasim | 2023-07-28 09:41 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
797 | 61C3AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6181548,24.9748054 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZSO-2572/25-ZSC-2572 | CD_25-ZS-2572 | POSITION SWITCH, SHUTDOWN VALVE 25-MOV-2522 BYPASS LINE | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 797 | Ashik Kasim | 2023-07-28 09:44 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
798 | C7C0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6182017,24.9748444 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PDIT-2522 | CA_25-PDIT-2522 | DP TRANSMITTER, 25-XV-2572 | Rosemount | 300S1AAD1E7M5 | 942290 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T5 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 798 | Ashik Kasim | 2023-07-28 10:01 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
799 | 8FBEAB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6180983,24.9747952 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-216 | CD_25-MOV-216 | MOV - 25-C-202 HP SECTION INLET | BIFFI | WGR3200 + ICON-020/180-144 (3000 Series) | 192273E006001 | Electrical | Not Available | Gb | IEC | Ex d. h ia | IIB | T4 | IP66/68 | -20 +85 | INE | IECEx INE 18.0026X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 799 | Ashik Kasim | 2023-07-31 11:22 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
800 | B1BEAB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6180575,24.9747727 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-216-ISO | 25-PC-109A | ISOLATOR, MOTOR OPERATED VALVE 25-MOV-216 | TECHNOR | CPSG-26/EFSRC-420 | 20P0092450022 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 800 | Ashik Kasim | 2023-07-31 05:51 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
801 | 56C1AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6179926,24.9747829 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FIT-202A | CA_25-FIT-202A | FLOW TRANSMITTER, MULTI ENVELOPE COMPRESSOR 2 -HP SECTION | Rosemount | Not Available | 0500185 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 09.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 801 | Ashik Kasim | 2023-07-31 05:56 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
802 | 67C1AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6179689,24.9747895 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FIT-202B | CA_25-FIT-202B | FLOW TRANSMITTER, MULTI ENVELOPE COMPRESSOR 2 -HP SECTION | Rosemount | Not Available | 0500191 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 09.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 802 | Ashik Kasim | 2023-07-31 06:00 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
803 | C9C2AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.617964,24.9747775 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-203 | CA_25-TIT-203 | TEMPERATURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 2 -HP SECTION | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 0944304 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close | B6. Broken earth connection | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 803 | Ashik Kasim | 2023-07-31 06:05 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-24 06:33
804 | 3395A64E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6179463,24.9747337 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-209 | CA_25-PIT-209 | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 2 -HP SECTION | Rosemount | 300S1AAD1E7M5 | 942202 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 804 | Ashik Kasim | 2023-07-31 06:11 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
805 | 24C2AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6179952,24.974794 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-208 | CA_25-PIT-208 | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 2 -HP SECTION | Rosemount | 300S1AAD1E7M5 | 942201 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 805 | Ashik Kasim | 2023-07-31 06:16 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
806 | F1C1AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6178816,24.9747463 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-203 | CA_25-PIT-203 | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 2 -HP SECTION | Rosemount | 3051TG4A2B21BWR3B4E7D4M5Q4Q8S5QT | 0500056 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 09.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 806 | Ashik Kasim | 2023-07-31 06:22 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
807 | 6FC0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6178749,24.9747328 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-201 | CA_25-PIT-201 | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 2 - LP SECTION | Rosemount | 3051TG4A2B21BWR3B4E7D4M5Q4Q8S5QT | 0500055 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 09.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 807 | Ashik Kasim | 2023-07-31 06:25 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
808 | FCC2AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6179653,24.9747857 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-207 | CA_25-PIT-207 | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 2 -LP SECTION | Rosemount | 300S1AAD1E7M5 | 942197 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close | B6. Broken earth connection | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 808 | Ashik Kasim | 2023-07-31 06:29 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-08-24 06:46
809 | 47C0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6179302,24.9748289 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-201 | CA_25-TIT-201 | TEMPERATURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 2 -HP SECTION | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 03587950 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 809 | Ashik Kasim | 2023-07-31 06:33 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
810 | C4BFAB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6179553,24.9748241 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-205 | CA_25-PIT-205 | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 2 - LP SECTION | Rosemount | 3051TG4A2B21BWR3B4E7D4M5Q4Q8S5QT | 0500180 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 09.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 810 | Ashik Kasim | 2023-07-31 06:35 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
811 | 7CC1AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6181483,24.9747949 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZS-200 | CD_25-ZS-200 | POSITION SWITCH, SHUTDOWN VALVE INLET MEC-2 (25-C-201/202) | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 811 | Ashik Kasim | 2023-07-31 08:20 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
812 | B6BEAB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6181584,24.9748292 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-200 | CD_25-XY-200 | SOLENOID VALVE, SHUTDOWN VALVE INLET MEC-2 (25-C-201/202) | Bifold | FP06P-77A | FL10919-0368 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 812 | Ashik Kasim | 2023-07-31 08:24 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
813 | A7C5AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6180294,24.9747937 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-205 | CD_25-XY-205 | SOLENOID VALVE, MEC 2 HOT GAS BYPASS - HP STAGE | ASCO | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex d | IIC | T6 | IP67 | -50 +60 | LCIE | IECEx LCIE07.0015X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 813 | Ashik Kasim | 2023-07-31 08:39 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
814 | 0FC2AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6180076,24.9747986 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FZSO-205/25-FZSC-205 | CD_25-ZS-205 | POSITION SWITCH , MEC 2 HOT GAS BYPASS VALVE- HP STAGE 25-XY-205 | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 814 | Ashik Kasim | 2023-07-31 08:43 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
815 | 0A8BAA4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6180662,24.974801 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-204 | CD_25-XY-204 | SOLENOID VALVE, MEC 2 HOT GAS BYPASS - LP STAGE | ASCO | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex d | IIC | T6 | IP67 | -50 +60 | LCIE | IECEx LCIE07.0015X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 815 | Ashik Kasim | 2023-07-31 08:56 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
816 | 03C0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6180076,24.9747986 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FZSO-204/25-FZSC-204 | CD_25-ZS-204 | POSITION SWITCH , MEC 2 HOT GAS BYPASS VALVE- LP STAGE 25-XY-204 | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 816 | Ashik Kasim | 2023-07-31 09:00 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
817 | C8C0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6178326,24.9748601 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2525T | CA_25-AE-2525T | FLAMMABLE GAS DETECTOR - OPEN PATH TYPE TRANSMITTER | Eye Safe | Quasar 900 | Not visible | Instrumentation | Not Applicable | Gb | IEC | Ex d | IIB + H2 | T4 | IP64 | -40 +75 | FMG | IECEx12.0007X | Yes | Others | Periodic | d | Close | A10. Wrong type blanking elements installed | A10. Replace with suitable type blanking elements | Teflon tape used along with Stop plugs | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 817 | Ashik Kasim | 2023-07-31 09:15 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-08-28 09:04
818 | 0BC2AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6179854,24.9747859 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FIT-201B | CA_25-FIT-201B | FLOW TRANSMITTER, MULTI ENVELOPE COMPRESSOR 2 - LP SECTION | Rosemount | Not Available | 0500190 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 09.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 818 | Ashik Kasim | 2023-07-31 09:36 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
819 | 99C0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6179633,24.9748345 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FIT-201A | CA_25-FIT-201A | FLOW TRANSMITTER, MULTI ENVELOPE COMPRESSOR 2 - LP SECTION | Rosemount | Not Available | 0500184 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 09.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 819 | Ashik Kasim | 2023-07-31 09:40 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
820 | 56C4AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6182256,24.9747446 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PDIT-201 | CA_25-PDIT-201 | DP TRANSMITTER, 25-C-201 LP SECTION INLET FILTER | Rosemount | 300S1AAD1E7M5 | 942298 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T5 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 820 | Ashik Kasim | 2023-07-31 09:48 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
821 | 34C0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6179541,24.97479 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PDIT-202 | CA_25-PDIT-202 | DP TRANSMITTER, 25-C-202 HP SECTION INLET FILTER | Rosemount | 300S1AAD1E7M5 | 942299 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T5 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 821 | Ashik Kasim | 2023-07-31 09:50 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
822 | 58C3AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6179977,24.9748268 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-206 | CA_25-PIT-206 | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 2 -HP SECTION | Rosemount | 3051TG4A2B21BWR3B4E7D4M5Q4Q8S5QT | 0500177 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 09.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 822 | Ashik Kasim | 2023-07-31 09:53 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
823 | 2CC0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6179722,24.9748795 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-208 | CA_25-TIT-208 | TEMPERATURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 2 -HP SECTION | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 03587960 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 823 | Ashik Kasim | 2023-07-31 09:59 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
824 | F0C0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6179502,24.9748024 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-204A | CA_25-TIT-204A | TEMPERATURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 2 -HP SECTION | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 03587961 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 824 | Ashik Kasim | 2023-07-31 10:02 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
825 | 2DC2AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.617951,24.9748297 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-204A | CA_25-PIT-204A | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 2 -HP SECTION | Rosemount | 300S1AAD1E7M5 | 942203 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 825 | Ashik Kasim | 2023-07-31 10:05 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
826 | 53C1AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6179566,24.9748492 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-204B | CA_25-PIT-204B | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 2 -HP SECTION | Rosemount | 300S1AAD1E7M5 | 942204 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 826 | Ashik Kasim | 2023-07-31 10:07 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
827 | B2BEAB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.617999,24.9747959 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-204C | CA_25-PIT-204C | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 2 -HP SECTION | Rosemount | 300S1AAD1E7M5 | 942205 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 827 | Ashik Kasim | 2023-07-31 10:08 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
828 | D2C5AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6179432,24.9748024 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-204B | CA_25-TIT-204B | TEMPERATURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 2 -HP SECTION | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 03587962 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 828 | Ashik Kasim | 2023-07-31 10:12 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
829 | FAC0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.617958,24.9748288 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-204C | CA_25-TIT-204C | TEMPERATURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 2 -HP SECTION | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 03587963 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 829 | Ashik Kasim | 2023-07-31 10:14 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
830 | C4C2AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6179944,24.9748705 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2524 | CA_25-AE-2524 | FLAMMABLE GAS DETECTOR - IR POINT TYPE | Net Safety | SC311S-100-ASSY | 0085909 | Instrumentation | Not Available | Gb | IEC | Ex db | IIB + H2 | T5 | IP64 | -40 +75 | FMG | IECEx FMG 12.0007X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 830 | Ashik Kasim | 2023-07-31 10:38 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
831 | 36C1AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6179172,24.9747763 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-207 | CA_25-TIT-207 | TEMPERATURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 2 - LP SECTION | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 03587951 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 831 | Ashik Kasim | 2023-08-01 05:39 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
832 | 2EC0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6180658,24.9749188 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-202A | CA_25-PIT-202A | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 2 - LP SECTION | Rosemount | 300S1AAD1E7M5 | 942198 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 832 | Ashik Kasim | 2023-08-01 05:45 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
833 | 95C1AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6179506,24.9747966 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-202B | CA_25-PIT-202B | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 2 - LP SECTION | Rosemount | 300S1AAD1E7M5 | 942199 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 833 | Ashik Kasim | 2023-08-01 05:48 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
834 | E2BFAB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6179493,24.9747813 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-202C | CA_25-PIT-202C | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 2 - LP SECTION | Rosemount | 300S1AAD1E7M5 | 942206 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 834 | Ashik Kasim | 2023-08-01 05:49 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
835 | 04C6AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6179172,24.9747763 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-202A | CA_25-TIT-202A | TEMPERATURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 2 - LP SECTION | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 03587955 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 835 | Ashik Kasim | 2023-08-01 05:52 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
836 | FBC0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6179536,24.9747551 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-202B | CA_25-TIT-202B | TEMPERATURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 2 - LP SECTION | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 03587957 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 836 | Ashik Kasim | 2023-08-01 05:53 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
837 | 57C3AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6179351,24.974757 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-202C | CA_25-TIT-202C | TEMPERATURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 2 - LP SECTION | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 03587959 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 837 | Ashik Kasim | 2023-08-01 05:56 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
838 | 72BEAB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.618014,24.9749008 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-BAL-204 | 25-PC-456 | LED AREA LIGHTING, 25-MCB-DB-002F9 | EATON | FMVA16LCY-UNV1-76-M20 | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 div 2 | Not Available | T4A | Not Available | 60 | UL | Not Available | Not applicable | Lighting | Periodic | d | Close | A6. Equipment id not available | A6. Fix equipment id |  | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 838 | Ashik Kasim | 2023-08-01 06:03 | A6. Pending | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable
839 | 8EC4AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area (+15) | 55.6178855,24.9747815 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-111 | 25-PC-455 | LIGHTING JUNCTION BOX | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040375 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 839 | Ashik Kasim | 2023-08-01 06:08 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
840 | 8BC1AB4E080104E0 |  | Margham | Area 25 | MEC 02 GC Motor Cooler Area | 55.6182127,24.9748489 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 27-JB-227 | CD_25-E220A/B | Junction Box | Technor | SB-273516 | I/19/20942 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T6 | Not Available | -20 +60 | IMQ | IECEx IMQ 15.0002X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 840 | Ashik Kasim | 2023-08-01 06:15 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
841 | 37C0AB4E080104E0 |  | Margham | Area 25 | MEC 02 GC Motor Cooler Area | 55.6181225,24.9748864 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-220A | 25-PC-021A | ISOLATOR, MOTOR 25-M-220A | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440023 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 841 | Ashik Kasim | 2023-08-01 06:19 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
842 | AEC0AB4E080104E0 |  | Margham | Area 25 | MEC 02 GC Motor Cooler Area | 55.6182136,24.9748789 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-220B | 25-PC-023A | ISOLATOR, MOTOR 25-M-220B | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440017 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 842 | Ashik Kasim | 2023-08-01 06:21 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
843 | FCC1AB4E080104E0 |  | Margham | Area 25 | MEC 02 GC Motor Cooler Area | 55.6182446,24.9749324 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HS-221C | CD_25-HS-221C | Exd Hand Switch -M-220-A | Cortem Group | EFSCO-64 | 19/343215 | Electrical | 2 | Gb | IEC | Ex db | IIC | T5 | IP66 | -20 +55 | CESI | CESI01ATEX092X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 843 | Ashik Kasim | 2023-08-01 06:24 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
844 | 56C3AB4E080104E0 |  | Margham | Area 25 | MEC 02 GC Motor Cooler Area | 55.6181873,24.9748852 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HS-222C | CD_25-HS-222C | Exd Hand Switch -M-220-B | Cortem Group | EFSCO-64 | 19/343215 | Electrical | 2 | Gb | IEC | Ex db | IIC | T5 | IP66 | -20 +55 | CESI | CESI01ATEX092X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 844 | Ashik Kasim | 2023-08-01 06:24 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
845 | 25C2AB4E080104E0 |  | Margham | Area 25 | MEC 02 GC Motor Cooler Area | 55.6181348,24.9752251 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-220A | 25-PC-020 | MOTOR, MEC 2 COOLING GAS AIR COOLER 1, 25-E-220A | WEG | W22XdBE | 24ABR20191048686432 | Electrical | 2 | Gb | IEC | Ex de | IIB | T4 | Not Available | -40 +60 | Baseefa | Baseefa13ATEX028X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 845 | Ashik Kasim | 2023-08-01 06:35 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
846 | CDC0AB4E080104E0 |  | Margham | Area 25 | MEC 02 GC Motor Cooler Area | 55.6181456,24.9749569 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-VSH-221 | CD_25-VSH-221 | VIBROSWITCH, MOTOR, MEC 2 COOLING GAS AIR COOLER 1, 25-E-220A | METRIC | 5550-411-040 | 778235 | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 846 | Ashik Kasim | 2023-08-01 06:38 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
847 | DBBEAB4E080104E0 |  | Margham | Area 25 | MEC 02 GC Motor Cooler Area | 55.6181662,24.9749035 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2554 | CA_25-AE-2554 | TRIPLE IR FLAME DETECTOR | Rosemount | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T4 | IP68 | -60 +85 | Sira | Sira15ATEX1364X | Yes | Others | Periodic | d | Close | A10. Wrong type blanking elements installed | A10. Replace with suitable type blanking elements | Teflon tape used | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 847 | Ashik Kasim | 2023-08-01 08:12 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-08-18 11:19
848 | E4BEAB4E080104E0 |  | Margham | Area 25 | MEC 02 GC Motor Cooler Area | 55.6182197,24.9749961 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2553 | CA_25-AE-2553 | TRIPLE IR FLAME DETECTOR | Rosemount | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T4 | IP68 | -60 +85 | Sira | Sira15ATEX1364X | Yes | Others | Periodic | d | Close | A10. Wrong type blanking elements installed | A10. Replace with suitable type blanking elements | Teflon tape used | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 848 | Ashik Kasim | 2023-08-01 08:22 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-08-18 11:23
849 | 38C0AB4E080104E0 |  | Margham | Area 25 | MEC 02 GC Motor Cooler Area | 55.6181354,24.9749296 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-220B | 25-PC-022 | MOTOR, MEC 2 COOLING GAS AIR COOLER 1, 25-E-220B | WEG | W22XdBE | 24ABR20191048686431 | Electrical | 2 | Gb | IEC | Ex de | IIB | T4 | Not Available | -40 +60 | Baseefa | Baseefa13ATEX028X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 849 | Ashik Kasim | 2023-08-01 08:30 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
850 | DBBFAB4E080104E0 |  | Margham | Area 25 | MEC 02 GC Motor Cooler Area | 55.618157,24.9749004 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-VSH-222 | CD_25-VSH-222 | VIBROSWITCH, MOTOR, MEC 2 COOLING GAS AIR COOLER 1, 25-E-220A | METRIC | 5550-411-040 | 778234 | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 850 | Ashik Kasim | 2023-08-01 08:33 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
851 | 3CC2AB4E080104E0 |  | Margham | Area 25 | MEC 02 GC Motor Cooler Area | 55.6180318,24.9748417 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2527 | CA_25-AE-2527 | FLAMMABLE GAS DETECTOR - IR POINT TYPE | Net Safety | SC311S-100-ASSY | 085910 | Instrumentation | Not Available | Gb | IEC | Ex d | IIB + H2 | T5 | IP64 | -40 +75 | FMG | IECExFMG 12.0007X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 851 | Ashik Kasim | 2023-08-01 08:38 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
852 | 68C1AB4E080104E0 |  | Margham | Area 25 | MEC 02 GC Motor Cooler Area | 55.6180541,24.9748586 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2523 | CA_25-AE-2523 | FLAMMABLE GAS DETECTOR - IR POINT TYPE | Net Safety | SC311S-100-ASSY | 085908 | Instrumentation | Not Available | Gb | IEC | Ex d | IIB + H2 | T5 | IP64 | -40 +75 | FMG | IECExFMG 12.0007X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 852 | Ashik Kasim | 2023-08-01 08:40 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
853 | 9CC1AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area-Ground | 55.6182139,24.9749308 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-DJBS-2521 | CD_25-DJBS-2521 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039888 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 853 | Ashik Kasim | 2023-08-01 08:45 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
854 | 22C2AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area-Ground | 55.6181017,24.9749304 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-DJBD-2522 | CD_25-DJBD-2522 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039927 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 854 | Ashik Kasim | 2023-08-01 08:48 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
855 | 66C2AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area-Ground | 55.6181368,24.9749146 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-DJBD-2521 | CD_25-DJBD-2521 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039936 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 855 | Ashik Kasim | 2023-08-01 08:50 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
856 | E8C1AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area-Ground | 55.6181282,24.97489 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FJBD-2521 | CD_25-FJBD-2521 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039901 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 856 | Ashik Kasim | 2023-08-01 08:52 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
857 | BDC4AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area-Ground | 55.61812,24.9748786 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-UJBD-2521 | CD_25-UJBD-2521 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039932 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 857 | Ashik Kasim | 2023-08-01 08:54 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
858 | 5DC2AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area-Ground | 55.6180527,24.9748683 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-UJBS-2523 | CD_25-UJBS-2523 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039947 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 858 | Ashik Kasim | 2023-08-01 08:58 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
859 | 74C0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area-Ground | 55.618,24.9748482 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FJBS-2521 | CD_25-FJBS-2521 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039921 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 859 | Ashik Kasim | 2023-08-01 08:59 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
860 | 76C0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area-Ground | 55.6178924,24.9748495 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-UJBS-2521 | CD_25-UJBS-2521 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039946 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 860 | Ashik Kasim | 2023-08-01 09:16 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
861 | 57BEAB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area-Ground | 55.6181247,24.9747218 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-UJBD-2521 | CD_25-UJBD-2521 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039917 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 861 | Ashik Kasim | 2023-08-01 09:23 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
862 | C4C0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6139809,24.9723813 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-301A | 25-PC-089A | ISOLATOR, MOTOR 25-M-301A | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440025 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 862 | Ashik Kasim | 2023-08-02 05:46 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
863 | 6CC1AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6184265,24.9747442 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-301C | 25-PC-093A | ISOLATOR, MOTOR 25-M-301C | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440007 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 863 | Ashik Kasim | 2023-08-02 05:47 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
864 | 7DBEAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.618437,24.9747028 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-301E | 25-PC-097A | ISOLATOR, MOTOR 25-M-301E | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440027 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 864 | Ashik Kasim | 2023-08-02 05:49 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
865 | 95BEAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6184104,24.9746654 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-301B | 25-PC-091B | ISOLATOR, MOTOR 25-M-301B | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440009 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 865 | Ashik Kasim | 2023-08-02 05:52 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
866 | 5C5CAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6183743,24.9746393 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-301D | 25-PC-095A | ISOLATOR, MOTOR 25-M-301D | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440020 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 866 | Ashik Kasim | 2023-08-02 06:01 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
867 | 2AC0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6186556,24.9744967 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-301F | 25-PC-099A | ISOLATOR, MOTOR 25-M-301F | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440001 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 867 | Ashik Kasim | 2023-08-02 06:01 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
868 | 03C1AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6184684,24.9745562 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-302A | 25-PC-101A | ISOLATOR, MOTOR 25-M-302A | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440034 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 868 | Ashik Kasim | 2023-08-02 06:03 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
869 | 59C4AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6185264,24.9744589 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-302B | 25-PC-103A | ISOLATOR, MOTOR 25-M-302B | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440002 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 869 | Ashik Kasim | 2023-08-02 06:04 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
870 | C55BAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.618521,24.9744753 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-302C | 25-PC-105A | ISOLATOR, MOTOR 25-M-302A | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440033 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 870 | Ashik Kasim | 2023-08-02 06:06 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
871 | 4BBEAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6184985,24.9747049 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HS-2528 | CD_25-HS-2528 | MANUAL CALL POINT | EATON | SM87PBLD | 2156858197111 | Instrumentation | Not Available | Gb | IEC | Ex d | IIC | T5 | IP66/67 | -55 +70 | BAS | IECEx BAS 09.0060 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 871 | Ashik Kasim | 2023-08-02 06:20 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
872 | 5CC3AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler-Ground | 55.6183403,24.9747331 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HS-2539 | CD_25-HS-2539 | MANUAL CALL POINT | EATON | SM87PBLD | 2156858197116 | Instrumentation | Not Available | Gb | IEC | Ex d | IIC | T5 | IP66/67 | -55 +70 | BAS | IECEx BAS 09.0060 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 872 | Ashik Kasim | 2023-08-02 06:24 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
873 | A2BEAB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Area-Ground | 55.6182321,24.9747003 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HS-2527 | CD_25-HS-2527 | MANUAL CALL POINT | EATON | SM87PBLD | 2156858197110 | Instrumentation | Not Available | Gb | IEC | Ex d | IIC | T5 | IP66/67 | -55 +70 | BAS | IECEx BAS 09.0060 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 873 | Ashik Kasim | 2023-08-02 06:26 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
874 | 88C1AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6184003,24.9746995 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-VJBD-2531 | CD_25-VJBD-2531 | JUNCTION BOX FOR LP DISCHARGE COOLERS | STAHL | 8150/1-0200-0300-150-3321 | Not Available | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T4 | IP66 | -60 +70 | PTB | PTB09ATEX1108 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 874 | Ashik Kasim | 2023-08-02 06:34 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
875 | 9FBEAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6183678,24.9746514 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-VJBD-2532 | CD_25-VJBD-2532 | JUNCTION BOX FOR HP DISCHARGE COOLERS | STAHL | 8150/1-0200-0300-150-3321 | Not Available | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T4 | IP66 | -60 +70 | PTB | PTB09ATEX1108 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 875 | Ashik Kasim | 2023-08-02 06:36 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
876 | 7CBFAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6185379,24.9747168 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-301C | 25-PC-092A | MOTOR, LP DISCHARGE COOLER, 25-E-301A | ABB | 3GGP222220-AOL+VC | 3G1F1915583339 | Electrical | 3 | Gc | IEC | Ex ec | IIC | T3 | IP65 | -20 +60 | DEMKO | DEMKO18ATEX2076X | Yes | Motor | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 876 | Ashik Kasim | 2023-08-02 08:38 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
877 | F57CAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6184496,24.974677 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XSSH-301C | CD_25-XSSH-301C | VIBROSWITCH, MOTOR, LP DISCHARGE COOLER, 25-E-301A | METRIC | 5550-421-041 | 780253 | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 877 | Ashik Kasim | 2023-08-02 09:05 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
878 | E8C0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6183788,24.9746591 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-301A | 25-PC-088A | MOTOR, LP DISCHARGE COOLER, 25-E-301A | ABB | 3GGP222220-AOL+VC | 3G1F1915583337 | Electrical | 3 | Gc | IEC | Ex ec | IIC | T3 | IP65 | -20 +60 | DEMKO | DEMKO18ATEX2076X | Yes | Motor | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 878 | Ashik Kasim | 2023-08-02 08:46 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
879 | E5C0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6183876,24.9746394 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XSSH-301A | CD_25-XSSH-301A | VIBROSWITCH, MOTOR, LP DISCHARGE COOLER, 25-E-301A | METRIC | 5550-421-041 | 780252 | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 879 | Ashik Kasim | 2023-08-02 09:13 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
880 | D5C5AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6186171,24.9747475 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-301E | 25-PC-096A | MOTOR, LP DISCHARGE COOLER, 25-E-301A | ABB | 3GGP222220-AOL+VC | 3G1F1915583341 | Electrical | 3 | Gc | IEC | Ex ec | IIC | T3 | IP65 | -20 +60 | DEMKO | DEMKO18ATEX2076X | Yes | Motor | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 880 | Ashik Kasim | 2023-08-02 09:23 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
881 | F3C2AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.618583,24.9746563 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XSSH-301E | CD_25-XSSH-301E | VIBROSWITCH, MOTOR, LP DISCHARGE COOLER, 25-E-301A | METRIC | 5550-421-041 | 780251 | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 881 | Ashik Kasim | 2023-08-02 09:28 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
882 | 61C0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6185792,24.9744867 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-301D | 25-PC-094A | MOTOR, LP DISCHARGE COOLER, 25-E-301B | ABB | 3GGP222220-AOL+VC | 3G1F1915583340 | Electrical | 3 | Gc | IEC | Ex ec | IIC | T3 | IP65 | -20 +60 | DEMKO | DEMKO18ATEX2076X | Yes | Motor | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 882 | Ashik Kasim | 2023-08-02 09:38 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
883 | BFBFAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6184069,24.9745684 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-301B | 25-PC-090A | MOTOR, LP DISCHARGE COOLER, 25-E-301B | ABB | 3GGP222220-AOL+VC | 3G1F1915583338 | Electrical | 3 | Gc | IEC | Ex ec | IIC | T3 | IP65 | -20 +60 | DEMKO | DEMKO18ATEX2076X | Yes | Motor | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 883 | Ashik Kasim | 2023-08-02 09:45 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
884 | 40C2AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6183668,24.9745805 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XSSH-301D | CD_25-XSSH-301D | VIBROSWITCH, MOTOR, LP DISCHARGE COOLER, 25-E-301B | METRIC | 5550-421-041 | 780248 | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 884 | Ashik Kasim | 2023-08-02 09:43 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
885 | B5C4AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6183745,24.9745841 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XSSH-301B | CD_25-XSSH-301B | VIBROSWITCH, MOTOR, LP DISCHARGE COOLER, 25-E-301B | METRIC | 5550-421-041 | 780246 | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 885 | Ashik Kasim | 2023-08-02 09:49 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
886 | 8BBEAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6185619,24.9745694 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-301F | 25-PC-098A | MOTOR, LP DISCHARGE COOLER, 25-E-301B | ABB | 3GGP222220-AOL+VC | 3G1F1915583342 | Electrical | 3 | Gc | IEC | Ex ec | IIC | T3 | IP65 | -20 +60 | DEMKO | DEMKO18ATEX2076X | Yes | Motor | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 886 | Ashik Kasim | 2023-08-02 09:52 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
887 | DBC5AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.618554,24.9745404 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XSSH-301F | CD_25-XSSH-301F | VIBROSWITCH, MOTOR, LP DISCHARGE COOLER, 25-E-301B | METRIC | 5550-421-041 | 780250 | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 887 | Ashik Kasim | 2023-08-02 09:54 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
888 | 38C2AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6184804,24.9745311 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-302B | 25-PC-102 | MOTOR, HP DISCHARGE COOLER, 25-E-302 | ABB | 3GGP222220-AOL+VC | 3G1F1915583193 | Electrical | 3 | Gc | IEC | Ex ec | IIC | T3 | IP65 | -20 +60 | DEMKO | DEMKO18ATEX2076X | Yes | Motor | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 888 | Ashik Kasim | 2023-08-02 09:59 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
889 | FDC0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6184849,24.974432 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XSSH-302B | CD_25-XSSH-302B | VIBROSWITCH, MOTOR, HP DISCHARGE COOLER, 25-E-302 | METRIC | 5550-421-041 | 780266 | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 889 | Ashik Kasim | 2023-08-02 10:02 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
890 | D1BFAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6183778,24.9744743 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-302A | 25-PC-100 | MOTOR, HP DISCHARGE COOLER, 25-E-302 | ABB | 3GGP222220-AOL+VC | 3G1F1915583192 | Electrical | 3 | Gc | IEC | Ex ec | IIC | T3 | IP65 | -20 +60 | DEMKO | DEMKO18ATEX2076X | Yes | Motor | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 890 | Ashik Kasim | 2023-08-02 10:06 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
891 | 63BEAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6183697,24.9744816 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XSSH-302A | CD_25-XSSH-302A | VIBROSWITCH, MOTOR, HP DISCHARGE COOLER, 25-E-302 | METRIC | 5550-421-041 | 780249 | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 891 | Ashik Kasim | 2023-08-02 10:08 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
892 | AFC1AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.618565,24.974491 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-302C | 25-PC-104 | MOTOR, HP DISCHARGE COOLER, 25-E-302 | ABB | 3GGP222220-AOL+VC | 3G1F1915583194 | Electrical | 3 | Gc | IEC | Ex ec | IIC | T3 | IP65 | -20 +60 | DEMKO | DEMKO18ATEX2076X | Yes | Motor | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 892 | Ashik Kasim | 2023-08-02 10:10 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
893 | B5C0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler Fan Deck (+15) | 55.6186896,24.9744949 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XSSH-302C | CD_25-XSSH-302C | VIBROSWITCH, MOTOR, HP DISCHARGE COOLER, 25-E-302 | METRIC | 5550-421-041 | 780247 | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 893 | Ashik Kasim | 2023-08-02 10:12 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
894 | DBC1AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6184961,24.9744945 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LCS-302C | 25-CC-134 | LCS - HP DISCHARGE COOLER MOTOR, 25-M-302C | BARTEC | 19D1009s/01 | 3937544-10-26 | Electrical | 2 | Gb | IEC | Ex db | IIB+H2 | T6 | IP66 | -5 +58 | DEKRA | DEKRA 13ATEX0209 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 894 | Ashik Kasim | 2023-08-03 05:39 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
895 | 0AC2AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6186401,24.9744629 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LCS-302B | 25-CC-131 | LCS - HP DISCHARGE COOLER MOTOR, 25-M-302B | BARTEC | 19D1009s/01 | 3937544-10-17 | Electrical | 2 | Gb | IEC | Ex db | IIB+H2 | T6 | IP66 | -5 +58 | DEKRA | DEKRA 13ATEX0209 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 895 | Ashik Kasim | 2023-08-03 05:42 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
896 | 2BC3AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6184852,24.974531 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LCS-302A | 25-CC-128 | LCS - HP DISCHARGE COOLER MOTOR, 25-M-302A | BARTEC | 19D1009s/01 | 3937544-10-15 | Electrical | 2 | Gb | IEC | Ex db | IIB+H2 | T6 | IP66 | -5 +58 | DEKRA | DEKRA 13ATEX0209 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 896 | Ashik Kasim | 2023-08-03 05:44 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
897 | C0BEAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6184826,24.9745286 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LCS-301F | 25-CC-125 | LCS - LP DISCHARGE COOLER MOTOR, 25-M-301F | BARTEC | 19D1009s/01 | 3937544-10-24 | Electrical | 2 | Gb | IEC | Ex db | IIB+H2 | T6 | IP66 | -5 +58 | DEKRA | DEKRA 13ATEX0209 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 897 | Ashik Kasim | 2023-08-03 05:47 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
898 | 25C3AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6184955,24.9745924 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LCS-301D | 25-CC-119 | LCS - LP DISCHARGE COOLER MOTOR, 25-M-301D | BARTEC | 19D1009s/01 | 3937544-10-12 | Electrical | 2 | Gb | IEC | Ex db | IIB+H2 | T6 | IP66 | -5 +58 | DEKRA | DEKRA 13ATEX0209 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 898 | Ashik Kasim | 2023-08-03 05:49 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
899 | 24C4AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6184678,24.9745988 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LCS-301B | 25-CC-113 | LCS - LP DISCHARGE COOLER MOTOR, 25-M-301B | BARTEC | 19D1009s/01 | 3937544-10-02 | Electrical | 2 | Gb | IEC | Ex db | IIB+H2 | T6 | IP66 | -5 +58 | DEKRA | DEKRA 13ATEX0209 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 899 | Ashik Kasim | 2023-08-03 05:52 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
900 | 87C0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6184672,24.9746922 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LCS-301E | 25-CC-122 | LCS - LP DISCHARGE COOLER MOTOR, 25-M-301E | BARTEC | 19D1009s/01 | 3937544-10-13 | Electrical | 2 | Gb | IEC | Ex db | IIB+H2 | T6 | IP66 | -5 +58 | DEKRA | DEKRA 13ATEX0209 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 900 | Ashik Kasim | 2023-08-03 05:56 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
901 | DABEAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6184037,24.9746481 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LCS-301C | 25-CC-116 | LCS - LP DISCHARGE COOLER MOTOR, 25-M-301C | BARTEC | 19D1009s/01 | 3937544-10-14 | Electrical | 2 | Gb | IEC | Ex db | IIB+H2 | T6 | IP66 | -5 +58 | DEKRA | DEKRA 13ATEX0209 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 901 | Ashik Kasim | 2023-08-03 05:58 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
902 | B9C3AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6184035,24.9746934 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LCS-301A | 25-CC-110 | LCS - LP DISCHARGE COOLER MOTOR, 25-M-301A | BARTEC | 19D1009s/01 | 3937544-10-27 | Electrical | 2 | Gb | IEC | Ex db | IIB+H2 | T6 | IP66 | -5 +58 | DEKRA | DEKRA 13ATEX0209 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 902 | Ashik Kasim | 2023-08-03 06:00 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
903 | 39C0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6185376,24.9744671 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HS-2538 | CD_25-HS-2538 | MANUAL CALL POINT | EATON | SM87PBLD | 2156858197115 | Instrumentation | Not Available | Gb | IEC | Ex d | IIC | T5 | IP66/67 | -55 +70 | BAS | IECEx BAS 09.0060 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 903 | Ashik Kasim | 2023-08-03 06:10 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
904 | C3BFAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6181929,24.9744549 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-300 | CA_25-TIT-300 | TEMPERATURE TRANSMITTER, AREA 25 COMPRESSOR C | Rosemount | 3144PD1A2E7B4M5CNC4Q4U1QTXAK1105 | 3587933 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECExFMG12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 904 | Ashik Kasim | 2023-08-03 06:13 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
905 | 6DBEAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6181428,24.9746318 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-300 | CA_25-PIT-300 | PRESSURE TRANSMITTER, AREA 25 COMPRESSOR C | Rosemount | 3051SAAD1E7M5 | 0942217 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECExKEM08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 905 | Ashik Kasim | 2023-08-03 06:18 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
906 | 56BEAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6183336,24.9746034 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FIT-300 | CA_25-FIT-300 | FLOW TRANSMITTER, AREA 25 COMPRESSOR C | Rosemount | 300S1AAD1E7M5 | 942625 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECExKEM08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 906 | Ashik Kasim | 2023-08-03 10:22 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
907 | EEC4AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler-Ground | 55.6183134,24.974666 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-305 | CA_25-TIT-305 | TEMPERATURE TRANSMITTER, LP DISCHARGE GAS COOLER | Rosemount | 3144PD1A2E7B4M5CNC4Q4U1QTXAK1105 | 3587984 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECExFMG12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 907 | Ashik Kasim | 2023-08-03 06:31 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
908 | F4BFAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6182825,24.9745418 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2566 | CA_25-AE-2566 | TRIPLE IR FLAME DETECTOR | Rosemount | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T4 | IP68 | -60 +85 | Sira | Sira15ATEX1364X | Yes | Others | Periodic | d | Close | A10. Wrong type blanking elements installed | A10. Replace with suitable type blanking elements | Teflon tape used | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 908 | Ashik Kasim | 2023-08-03 10:26 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-08-18 10:44
909 | 755DAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+30)Top | 55.6183457,24.9746764 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2565 | CA_25-AE-2565 | TRIPLE IR FLAME DETECTOR | Rosemount | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T4 | IP68 | -60 +85 | Sira | Sira15ATEX1364X | Yes | Others | Periodic | d | Close | A10. Wrong type blanking elements installed | A10. Replace with suitable type blanking elements | Requires maintenance support to complete repair job | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 909 | Ashik Kasim | 2023-08-03 08:22 | A10. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding
910 | EAC4AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6183365,24.9747279 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2526T | CA_25-AE-2526T | FLAMMABLE GAS DETECTOR - OPEN PATH TYPE TRANSMITTER | Eye Safe | Quasar 900 | Not visible | Instrumentation | Not Applicable | Gb | IEC | Ex d | IIB + H2 | T4 | IP64 | -40 +75 | FMG | IECEx12.0007X | Yes | Others | Periodic | d | Close | A10. Wrong type blanking elements installed | A10. Replace with suitable type blanking elements | Teflon tape used along with Stop plugs | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 910 | Ashik Kasim | 2023-08-03 08:47 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-08-18 09:06
911 | B8C0AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6183177,24.9747649 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-206 | CD_25-XY-206 | SOLENOID VALVE, SHUTDOWN VALVE OUTLET MEC-2 (25-C-201/202) | Bifold | FP06P-77A | FL10919-0374 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 911 | Ashik Kasim | 2023-08-03 08:56 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
912 | 93C1AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6183038,24.9747885 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZSO-206/25-ZSC-206 | CD_25-ZS-206 | POSITION SWITCH, SHUTDOWN VALVE OUTLET MEC-2 (25-C-201/202) | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 912 | Ashik Kasim | 2023-08-03 09:01 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
913 | ABBEAB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6183008,24.9747696 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-2521 | CA_25-PIT-2521 | PRESSURE TRANSMITTER, AREA 25 COMPRESSOR A | Rosemount | 300S1AAD1E7M5 | Not visible | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T5 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 913 | Ashik Kasim | 2023-08-03 09:16 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
914 | 5DC3AB4E080104E0 |  | Margham | Area 25 | MEC 02 Gas Cooler (+15) | 55.6183917,24.9749699 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2526R | CA_25-AE-2526R | FLAMMABLE GAS DETECTOR - OPEN PATH TYPE TRANSMITTER | Eye Safe | Quasar 900 | Not visible | Instrumentation | Not Applicable | Gb | IEC | Ex d | IIB + H2 | T4 | IP64 | -40 +75 | FMG | IECEx12.0007X | Yes | Others | Periodic | d | Close | A10. Wrong type blanking elements installed | A10. Replace with suitable type blanking elements | Teflon tape used along with Stop plugs | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 914 | Ashik Kasim | 2023-08-03 09:24 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-08-18 09:03
915 | 07C1AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183464,24.974626 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FZT-303 | CA_FY/FZT-303 | POSITION TRANSMITTER, ANTI-SURGE CONTROL VALVE 25-C-302 - PARALLEL MODE | STI | Not Available | P-1901611 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -40 +60 | Baseefa | Baseefa 11ATEX0158X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 915 | Ashik Kasim | 2023-08-03 09:39 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
916 | ABBFAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183329,24.9746145 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-303 | CD_25-XY-303 | Solenoid Valve -25-FV-303 | ASCO | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex d | IIC | T5 | IP66/67 | -40 +70 | LCIE | LCIE00ATEX6008X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 916 | Ashik Kasim | 2023-08-03 09:40 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
917 | 7ABFAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183293,24.9746128 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FZSC-303 | Not Available | Limit switch -Close- FCV-303 | Go switch | 22-11529-00M | 220906145734 | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T6 | IP66/68 | -40 +60 | Baseefa | Baseefa 12ATEX0160X | Yes | Others | Periodic | d | Close | A6. Circuit id not available | A6. Fix circuit id |  | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 917 | Ashik Kasim | 2023-08-03 09:42 | A6. Pending | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable
918 | FEBFAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183462,24.9746287 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FZSO-303 | Not Available | Limit switch -Open- FCV-303 | Go switch | 22-11529-00M | 220906101745 | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T6 | IP66/68 | -40 +60 | Baseefa | Baseefa 12ATEX0160X | Yes | Others | Periodic | d | Close | A6. Circuit id not available | A6. Fix circuit id |  | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 918 | Ashik Kasim | 2023-08-03 09:44 | A6. Pending | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable
919 | D5BFAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183392,24.9746206 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | Not Available | CD_25-ZS-303 | Junction Box -FCV-303 | Pepperl+Fuchs | ES2315S-0V | P221-256-02 | Instrumentation | 2 | Gb | IEC | Ex e | IIC | T6 | IP66 | -20 +55 | Sira | Sira09ATEX3135X | Yes | Others | Periodic | d | Close | A6. Equipment id not available | A6. Fix equipment id |  | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 919 | Ashik Kasim | 2023-08-03 09:48 | A6. Pending | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable
920 | 94C2AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183766,24.9745507 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FZT-302 | CA_FY/FZT-302 | POSITION TRANSMITTER, ANTI-SURGE CONTROL VALVE 25-C-301-SERIES MODE | STI | Not Available | P-1901621 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -40 +60 | Baseefa | Baseefa 11ATEX0158X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 920 | Ashik Kasim | 2023-08-03 09:52 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
921 | 1161AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183697,24.9746066 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-302 | CD_25-XY-302 | Solenoid Valve -25-FV-302 | ASCO | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex d | IIC | T5 | IP66/67 | -40 +70 | LCIE | LCIE00ATEX6008X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 921 | Ashik Kasim | 2023-08-03 09:56 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
922 | E4BFAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183719,24.9745827 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FZSC-302 | Not Available | Limit switch -Close- FCV-302 | Go switch | 22-11529-00M | 220906145739 | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T6 | IP66/68 | -40 +60 | Baseefa | Baseefa 12ATEX0160X | Yes | Others | Periodic | d | Close | A6. Circuit id not available | A6. Fix circuit id |  | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 922 | Ashik Kasim | 2023-08-03 09:57 | A6. Pending | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable
923 | 5BC3AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183229,24.9745857 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FZSO-302 | Not Available | Limit switch -Open- FCV-302 | Go switch | 22-11529-00M | 220906101700 | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T6 | IP66/68 | -40 +60 | Baseefa | Baseefa 12ATEX0160X | Yes | Others | Periodic | d | Close | A6. Circuit id not available | A6. Fix circuit id |  | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 923 | Ashik Kasim | 2023-08-03 09:59 | A6. Pending | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable
924 | D5C1AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183342,24.9745809 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-306 | CA_25-TIT-306 | TEMPERATURE TRANSMITTER, HP DISCHARGE GAS COOLER | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 3587930 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 924 | Ashik Kasim | 2023-08-03 10:01 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
925 | 9DC0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.618297,24.9745938 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | Not Available | CD_25-ZS-302 | Junction Box -FCV-302 | Pepperl+Fuchs | ES2315S-0V | P221-256-05 | Instrumentation | 2 | Gb | IEC | Ex e | IIC | T6 | IP66 | -20 +55 | Sira | Sira09ATEX3135X | Yes | Others | Periodic | d | Close | A6. Equipment id not available | A6. Fix equipment id |  | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 925 | Ashik Kasim | 2023-08-03 10:03 | A6. Pending | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable
926 | 29C2AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183193,24.9746682 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-318-ISO | 25-PC-114A | ISOLATOR, MOTOR OPERATED VALVE 25-MOV-318 | TECHNOR | CPSG-26/EFSRC-420 | 20P0092450024 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 926 | Ashik Kasim | 2023-08-04 05:38 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
927 | CFBFAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.618329,24.9746283 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-318 | CD_25-MOV-318 | MOV - PROCESS GAS COOLER OUTLET TO FINAL/INTERMEDIATE DISCHARGE HEADER | BIFFI | WGR3200 + ICON-020/180-144 (3000 Series) | 192273E001001 | Electrical | Not Available | Gb | IEC | Ex d. h ia | IIB | T4 | IP66/68 | -20 +85 | INE | IECEx INE 18.0026X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 927 | Ashik Kasim | 2023-08-04 05:42 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
928 | 68C0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183599,24.9745868 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-317-ISO | 25-PC-113A | ISOLATOR, MOTOR OPERATED VALVE 25-MOV-317 | TECHNOR | CPSG-26/EFSRC-420 | 20P0092450016 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 928 | Ashik Kasim | 2023-08-04 05:45 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
929 | E5C4AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183338,24.9745911 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-317 | CD_25-MOV-317 | MOV - PROCESS GAS COOLER OUTLET (25-E-301 A/B ) TO 25-C-302 | BIFFI | WGR3200 + ICON-020/180-144 (3000 Series) | 192273E002001 | Electrical | Not Available | Gb | IEC | Ex d. h ia | IIB | T4 | IP66/68 | -20 +85 | INE | IECEx INE 18.0026X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 929 | Ashik Kasim | 2023-08-04 05:47 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
930 | 605AAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183408,24.974594 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZSO-308/25-ZSC-308 | CD_25-ZS-308 | POSITION SWITCH , BLOWDOWN VALVE PROCESS GAS COOLER OUTLET (25-E-302 A/B) | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 930 | Ashik Kasim | 2023-08-04 05:52 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
931 | 80BFAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6182563,24.974601 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-308 | CD_25-XY-308 | SOLENOID VALVE, BLOWDOWN VALVE PROCESS GAS COOLER OUTLET (25-E-302 A/B) | Bifold | FP06P-77A | FL10919-0111 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 931 | Ashik Kasim | 2023-08-04 06:00 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
932 | C6BFAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183159,24.974515 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-2533-ISO | 25-PC-125A | ISOLATOR, MOTOR OPERATED VALVE 25-MOV-2533 | TECHNOR | CPSG-26/EFSRC-420 | 20P0092450008 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 932 | Ashik Kasim | 2023-08-04 06:05 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
933 | B7C3AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183467,24.9745278 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-2533 | CD_25-MOV-2533 | MOV - 25-E-301/2 A/B OUTLET MEC DISCHARGE HEADER | BIFFI | WGR3200 + ICON-020/180-144 (3000 Series) | 192273E001001 | Electrical | Not Available | Gb | IEC | Ex d. h ia | IIB | T4 | IP66/68 | -20 +85 | INE | IECEx INE 18.0026X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 933 | Ashik Kasim | 2023-08-04 06:09 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
934 | FAC2AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183262,24.9745084 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZSC-2583/25-ZSO-2583 | CD_25-ZS-2583 | POSITION SWITCH , SHUTDOWN VALVE 25-MOV-2533 BYPASS LINE | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 934 | Ashik Kasim | 2023-08-04 06:16 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
935 | C3C0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6182972,24.9745056 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-2583 | CD_25-XY-2583 | SOLENOID VALVE, SHUTDOWN VALVE 25-MOV-2533 BYPASS LINE | Bifold | FP06P-77A | FL10919-0372 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 935 | Ashik Kasim | 2023-08-04 06:19 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
936 | 87BEAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183486,24.9745299 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZSC-2584/25-ZSO-2584 | CD_25-ZS-2584 | POSITION SWITCH , SHUTDOWN VALVE 25-MOV-2533 BYPASS LINE | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 936 | Ashik Kasim | 2023-08-04 06:24 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
937 | 93C0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183366,24.9745437 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-2583 | CD_25-XY-2583 | SOLENOID VALVE, SHUTDOWN VALVE 25-MOV-2533 BYPASS LINE | Bifold | FP06P-77A | FL10919-0386 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 937 | Ashik Kasim | 2023-08-04 06:26 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
938 | D2BFAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183921,24.9745325 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-2534-ISO | 25-PC-126A | ISOLATOR, MOTOR OPERATED VALVE 25-MOV-2534 | TECHNOR | CPSG-26/EFSRC-420 | 20P0092450006 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 938 | Ashik Kasim | 2023-08-04 06:31 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
939 | 4ABEAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183295,24.9745001 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-2534 | CD_25-MOV-2534 | MOV - 25-E-301/2 A/B OUTLET TO MEC INTERCONNECTION HEADER | BIFFI | WGR3200 + ICON-020/180-144 (3000 Series) | 192273E0010001 | Electrical | Not Available | Gb | IEC | Ex d. h ia | IIB | T4 | IP66/68 | -20 +85 | INE | IECEx INE 18.0026X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 939 | Ashik Kasim | 2023-08-04 06:36 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
940 | 62C0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6182472,24.9746184 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-2531 | CA_25-PIT-2531 | PRESSURE TRANSMITTER, AREA 25 COMPRESSOR C | Rosemount | 300S1AAD1E7M5 | 942181 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T5 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 940 | Ashik Kasim | 2023-08-04 06:50 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
941 | 92C3AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183469,24.9746753 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2536R | CA_25-AE-2536R | FLAMMABLE GAS DETECTOR - OPEN PATH TYPE RECEIVER | Eye Safe | Quasar 900 | Not visible | Instrumentation | Not Applicable | Gb | IEC | Ex d | IIB + H2 | T4 | IP64 | -40 +75 | SIRA | IECEx SIR 13.0069X | Yes | Others | Periodic | d | Close | A10. Wrong type blanking elements installed | A10. Replace with suitable type blanking elements | Teflon tape used along with Stop plugs | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 941 | Ashik Kasim | 2023-08-04 08:16 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-08-18 09:18
942 | ADBEAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183845,24.9745248 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PDIT-2533 | CA_25-PDIT-2533 | DP TRANSMITTER, 25-XV-2583 | Rosemount | 300S1AAD1E7M5 | 942307 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T5 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 942 | Ashik Kasim | 2023-08-04 08:26 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
943 | ADBFAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.618373,24.9744385 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PDIT-2534 | CA_25-PDIT-2534 | DP TRANSMITTER, 25-XV-2584 | Rosemount | 300S1AAD1E7M5 | 942308 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T5 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 943 | Ashik Kasim | 2023-08-04 08:28 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
944 | 7FBEAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6181789,24.9745096 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-2509 | CA_25-PIT-2509 | PRESSURE TRANSMITTER, INSTRUMENT AIR SYSTEM | Rosemount | 300S1AAD1E7M5 | 0942220 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 944 | Ashik Kasim | 2023-08-04 10:02 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
945 | BCC3AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183113,24.9744708 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-306 | CD_25-XY-306 | SOLENOID VALVE, SHUTDOWN VALVE OUTLET MEC-2 (25-C-301/302) | Bifold | FP06P-77A | FL10919-0375 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 945 | Ashik Kasim | 2023-08-04 08:36 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
946 | 10C6AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183165,24.9744758 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZSO-306/25-ZSC-306 | CD_25-ZS-306 | POSITION SWITCH, SHUTDOWN VALVE OUTLET MEC-2 (25-C-301/302) | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 946 | Ashik Kasim | 2023-08-04 08:40 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
947 | EDC0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183571,24.9744635 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-2503 | CA_25-TIT-2503 | TEMPERATURE TRANSMITTER, DISCHARGE HEADER | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 3587934 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 947 | Ashik Kasim | 2023-08-04 08:46 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
948 | 3A5BAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183268,24.9744766 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZT-2500 | CA_25-ZT-2500 | POSITION TRANSMITTER, FLOW CHOKE VALVE ON MEC HEADER | Flowserve | 3200MD-33-N6-E-03-40-KS-OF | 7019001 | Instrumentation | Not Available | Not Available | IEC | Ex d | IIB + H2 | T5 | IP65 | -40 +55 | SIRA | IECEx SIR04.0023X | Yes | Others | Periodic | d | Close | A6. Equipment id not available | A6. Fix equipment id |  | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 948 | Ashik Kasim | 2023-08-04 09:00 | A6. Pending | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable
949 | DCBFAB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183415,24.9744869 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZSC-2509/25-ZSO-2509 | CD_25-ZS-2509 | POSITION SWITCH,, BLOWDOWN VALVE MEC DISCHARGE HEADER TO HP INJECTION | Topworx | TXS-P41GNPM | 190910215122 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 949 | Ashik Kasim | 2023-08-04 09:04 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
950 | 08C1AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183529,24.9744764 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-2509 | CD_25-XY-2509 | SOLENOID VALVE, BLOWDOWN VALVE MEC DISCHARGE HEADER TO HP INJECTION | Bifold | FP06P-77A | FL10919-0383 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 950 | Ashik Kasim | 2023-08-04 09:07 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
951 | 0DC2AB4E080104E0 |  | Margham | Area 25 | MEC 03 Gas Cooler (+15) | 55.6183592,24.9744607 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2536T | CA_25-AE-2536T | FLAMMABLE GAS DETECTOR - OPEN PATH TYPE RECEIVER | Eye Safe | Quasar 900 | Not visible | Instrumentation | Not Applicable | Gb | IEC | Ex d | IIB + H2 | T4 | IP64 | -40 +75 | SIRA | IECEx SIR 13.0069X | Yes | Others | Periodic | d | Close | A10. Wrong type blanking elements installed | A10. Replace with suitable type blanking elements | Teflon tape used along with Stop plugs | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 951 | Ashik Kasim | 2023-08-04 09:11 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-08-18 10:19
952 | F7C0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Pipeline Area- Ground | 55.6184146,24.9746392 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-UJBD-2534 | CD_25-UJBD-2534-01 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039915 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 952 | Ashik Kasim | 2023-08-04 09:37 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
953 | 05C6AB4E080104E0 |  | Margham | Area 25 | MEC 03 Pipeline Area- Ground | 55.6182981,24.9745967 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-UJBD-2533 | CD_25-UJBD-2533 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039942 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 953 | Ashik Kasim | 2023-08-04 09:39 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
954 | CD5AAB4E080104E0 |  | Margham | Area 25 | MEC 03 Pipeline Area- Ground | 55.618244,24.9746484 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-UJBD-2532 | CD_25-UJBD-2532 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039882 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 954 | Ashik Kasim | 2023-08-04 09:40 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
955 | 78BFAB4E080104E0 |  | Margham | Area 25 | MEC 03 Pipeline Area- Ground | 55.618261,24.9746306 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-DJBS-2532 | CD_25-DJBS-2532 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039896 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 955 | Ashik Kasim | 2023-08-04 09:43 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
956 | B4C0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Pipeline Area- Ground | 55.6181936,24.974664 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FJBS-2532 | CD_25-FJBS-2532 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039924 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 956 | Ashik Kasim | 2023-08-04 09:45 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
957 | 94C0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Pipeline Area- Ground | 55.6182522,24.9745884 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-DJBD-2534 | CD_25-DJBD-2534 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039930 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 957 | Ashik Kasim | 2023-08-04 09:47 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
958 | 64C1AB4E080104E0 |  | Margham | Area 25 | MEC 03 Pipeline Area- Ground | 55.6182701,24.9745478 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-DJBD-2533 | CD_25-DJBD-2533 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039939 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 958 | Ashik Kasim | 2023-08-04 09:51 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
959 | 54C3AB4E080104E0 |  | Margham | Area 25 | MEC 03 Pipeline Area- Ground | 55.6181869,24.9744977 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-DJBS-2500 | CD_25-DJBS-2500 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039883 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 959 | Ashik Kasim | 2023-08-07 05:36 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
960 | 31C0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Pipeline Area- Ground | 55.6182495,24.9745337 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-EJBS-2500 | CD_25-EJBS-2500 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039904 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 960 | Ashik Kasim | 2023-08-07 05:38 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
961 | 925AAB4E080104E0 |  | Margham | Area 25 | MEC 03 Pipeline Area- Ground | 55.6182021,24.974473 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-EJBD-2500 | CD_25-EJBD-2500 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039886 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 961 | Ashik Kasim | 2023-08-07 05:41 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
962 | C3C3AB4E080104E0 |  | Margham | Area 25 | MEC 03 Pipeline Area- Ground | 55.618254,24.9744437 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-UJBD-2535 | CD_25-UJBD-2535 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039892 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 962 | Ashik Kasim | 2023-08-07 05:44 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
963 | F1BFAB4E080104E0 |  | Margham | Area 25 | MEC 03 Pipeline Area- Ground | 55.6183282,24.9744231 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-DJBD-2500 | CD_25-DJBD-2500-01 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039943 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 963 | Ashik Kasim | 2023-08-07 05:46 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
964 | 2DC0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Pipeline Area- Ground | 55.6182775,24.9744415 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FJBS-2500 | CD_25-FJBS-2500 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039912 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 964 | Ashik Kasim | 2023-08-07 05:52 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
965 | AEC1AB4E080104E0 |  | Margham | Area 25 | MEC 03 GC Motor Cooler Area | 55.618338,24.9747193 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-320A | 25-PC-035 | MOTOR, MEC 3 COOLING GAS AIR COOLER 1, 25-E-320A | WEG | W22XdBE | 24ABR20191048686434 | Electrical | 2 | Gb | IEC | Ex de | IIB | T4 | Not Available | -40 +60 | Baseefa | Baseefa13ATEX028X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 965 | Ashik Kasim | 2023-08-07 05:56 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
966 | 40C0AB4E080104E0 |  | Margham | Area 25 | MEC 03 GC Motor Cooler Area | 55.6181958,24.9747026 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-VSH-321 | CD_25-VSH-321 | VIBROSWITCH, MOTOR, MEC 3 COOLING GAS AIR COOLER 1, 25-E-320A | METRIC | 5550-411-040 | 778231 | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 966 | Ashik Kasim | 2023-08-07 05:58 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
967 | DDBFAB4E080104E0 |  | Margham | Area 25 | MEC 03 GC Motor Cooler Area | 55.6181959,24.97461 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-M-320B | 25-PC-037 | MOTOR, MEC 3 COOLING GAS AIR COOLER 1, 25-E-320B | WEG | W22XdBE | 24ABR20191048686433 | Electrical | 2 | Gb | IEC | Ex de | IIB | T4 | Not Available | -40 +60 | Baseefa | Baseefa13ATEX028X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 967 | Ashik Kasim | 2023-08-07 06:00 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
968 | 335CAB4E080104E0 |  | Margham | Area 25 | MEC 03 GC Motor Cooler Area | 55.6181763,24.9746315 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-VSH-322 | CD_25-VSH-322 | VIBROSWITCH, MOTOR, MEC 3 COOLING GAS AIR COOLER 1, 25-E-320B | METRIC | 5550-411-040 | 778230 | Electrical | 2 | Gb | IEC | Ex d | IIB + H2 | T6 | IP65 | -40 +70 | Baseefa | Baseefa10ATEX0098 | Not applicable | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 968 | Ashik Kasim | 2023-08-07 06:02 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
969 | 0FC0AB4E080104E0 |  | Margham | Area 25 | MEC 03 GC Motor Cooler Area | 55.6181676,24.9747291 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2533 | CA_25-AE-2533 | FLAMMABLE GAS DETECTOR - IR POINT TYPE | Net Safety | SC311S-100-ASSY | 085913 | Instrumentation | Not Available | Gb | IEC | Ex d | IIB + H2 | T5 | IP64 | -40 +75 | FMG | IECExFMG 12.0007X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 969 | Ashik Kasim | 2023-08-07 06:06 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
970 | 6FBEAB4E080104E0 |  | Margham | Area 25 | MEC 03 GC Motor Cooler Area | 55.6181892,24.9746178 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2537 | CA_25-AE-2537 | FLAMMABLE GAS DETECTOR - IR POINT TYPE | Net Safety | SC311S-100-ASSY | 085915 | Instrumentation | Not Available | Gb | IEC | Ex d | IIB + H2 | T5 | IP64 | -40 +75 | FMG | IECExFMG 12.0007X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 970 | Ashik Kasim | 2023-08-07 06:08 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
971 | 0AC0AB4E080104E0 |  | Margham | Area 25 | MEC 03 GC Motor Cooler Area | 55.61826,24.9745401 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 27-JB-327 | CD_25-E320A/B | Junction Box | Technor | SB-273516 | I/19/20940 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T6 | Not Available | -20 +60 | IMQ | IECEx IMQ 15.0002X | Yes | Others | Periodic | e | Close | A10. Bolts missing | A10. Fix with manufacture recommended bolts |  | 1 |  | Yellow | 4 | Minor Repair Required | Normal Operations | Not Applicable |  | Data Sheet 971 | Ashik Kasim | 2023-08-07 06:27 | A10. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Normal Operations | Not Applicable
972 | 8CC3AB4E080104E0 |  | Margham | Area 25 | MEC 03 GC Motor Cooler Area | 55.618259,24.9745429 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-320A | 25-PC-036A | ISOLATOR, MOTOR 25-M-320A | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440004 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 972 | Ashik Kasim | 2023-08-07 06:18 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
973 | C2BEAB4E080104E0 |  | Margham | Area 25 | MEC 03 GC Motor Cooler Area | 55.618227,24.9745502 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IS-320B | 25-PC-038A | ISOLATOR, MOTOR 25-M-320B | TECHNOR | CPSG-26/EFSRC-220 | 20P0092440006 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 973 | Ashik Kasim | 2023-08-07 06:20 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
974 | B7BEAB4E080104E0 |  | Margham | Area 25 | MEC 03 GC Motor Cooler Area | 55.6182587,24.9746332 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HS-321C | CD_25-HS-321C | Exd Hand Switch -M-320-A | Cortem Group | EFSCO-64 | 19/343217 | Electrical | 2 | Gb | IEC | Ex db | IIC | T5 | IP66 | -20 +55 | CESI | CESI01ATEX092X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 974 | Ashik Kasim | 2023-08-07 06:23 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
975 | 84BEAB4E080104E0 |  | Margham | Area 25 | MEC 03 GC Motor Cooler Area | 55.6182698,24.9745763 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HS-321C | CD_25-HS-321C | Exd Hand Switch -M-320-A | Cortem Group | EFSCO-64 | 19/343216 | Electrical | 2 | Gb | IEC | Ex db | IIC | T5 | IP66 | -20 +55 | CESI | CESI01ATEX092X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 975 | Ashik Kasim | 2023-08-07 06:24 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
976 | 5E2CAA4E080104E0 |  | Margham | Area 25 | MEC 03 GC Motor Cooler Area | 55.6181278,24.974574 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2564 | CA_25-AE-2564 | TRIPLE IR FLAME DETECTOR | Rosemount | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T4 | IP68 | -60 +85 | Sira | Sira15ATEX1364X | Yes | Others | Periodic | d | Close | A10. Wrong type blanking elements installed | A10. Replace with suitable type blanking elements | Teflon tape used | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 976 | Ashik Kasim | 2023-08-07 06:32 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-08-18 11:14
977 | 7FC1AB4E080104E0 |  | Margham | Area 25 | MEC 03 GC Motor Cooler Area | 55.6181648,24.9746562 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2563 | CA_25-AE-2563 | TRIPLE IR FLAME DETECTOR | Rosemount | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T4 | IP68 | -60 +85 | Sira | Sira15ATEX1364X | Yes | Others | Periodic | d | Close | A10. Wrong type blanking elements installed | A10. Replace with suitable type blanking elements | Teflon tape used | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 977 | Ashik Kasim | 2023-08-07 06:37 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-08-18 11:18
978 | E0C0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6181505,24.9744965 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PDIT-2531 | CA_25-PDIT-2531 | DP TRANSMITTER, 25-XV-2581 | Rosemount | 300S1AAD1E7M5 | 942288 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T5 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 978 | Ashik Kasim | 2023-08-07 08:42 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
979 | CBC1AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6181541,24.9744545 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-2581 | CD_25-XY-2581 | SOLENOID VALVE, SHUTDOWN VALVE 25-MOV-2521 BYPASS LINE | Bifold | FP06P-77A | FL10919-0376 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 979 | Ashik Kasim | 2023-08-07 08:48 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
980 | 83C1AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6182025,24.9744739 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZSO-2581/25-ZSC-2581 | CD_25-ZS-2581 | POSITION SWITCH , SHUTDOWN VALVE 25-MOV-2522 BYPASS LINE | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 980 | Ashik Kasim | 2023-08-07 08:52 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
981 | 7DBFAB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6182145,24.9744704 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PDIT-300 | CA_25-PDIT-300 | DP TRANSMITTER, 25-XV-301 | Rosemount | 300S1AAD1E7M5 | 942300 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T5 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 981 | Ashik Kasim | 2023-08-07 08:58 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
982 | C7BFAB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6181485,24.974437 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-301 | CD_25-XY-301 | SOLENOID VALVE, SHUTDOWN VALVE 25-MOV-2521 BYPASS LINE | Bifold | FP06P-77A | FL10919-0360 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 982 | Ashik Kasim | 2023-08-07 09:05 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
983 | CA5CAB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.618133,24.9744635 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZSO-301/25-ZSC-301 | CD_25-ZS-301 | POSITION SWITCH, EQUALIZING VALVE ACROSS 25-XV-300 | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 983 | Ashik Kasim | 2023-08-07 09:11 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
984 | F1C0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6181783,24.9744556 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2535R | CA_25-AE-2535R | FLAMMABLE GAS DETECTOR - OPEN PATH TYPE RECEIVER | Eye Safe | Quasar 900 | Not visible | Instrumentation | Not Applicable | Gb | IEC | Ex d | IIB + H2 | T4 | IP64 | -40 +75 | SIRA | IECEx SIR 13.0069X | Yes | Others | Periodic | d | Close | A10. Wrong type blanking elements installed | A10. Replace with suitable type blanking elements | Teflon tape used along with Stop plugs | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 984 | Ashik Kasim | 2023-08-07 09:24 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-08-28 09:11
985 | 90C0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6181984,24.9745542 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-2532-ISO | 25-PC-124A | ISOLATOR, MOTOR OPERATED VALVE 25-MOV-2532 | TECHNOR | CPSG-26/EFSRC-420 | 20P0092450003 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 985 | Ashik Kasim | 2023-08-07 09:33 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
986 | 18C1AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6181264,24.9744747 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-2532 | CD_25-MOV-2532 | MOV - HP SUCTION HEADER-COMMON TO MEC 3 | BIFFI | WGR3200 + ICON-020/180-144 (3000 Series) | 192273E0012001 | Electrical | Not Available | Gb | IEC | Ex d. h ia | IIB | T4 | IP66/68 | -20 +85 | INE | IECEx INE 18.0026X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 986 | Ashik Kasim | 2023-08-07 09:36 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
987 | 1BC1AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6181721,24.9744821 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-2531-ISO | 25-PC-123A | ISOLATOR, MOTOR OPERATED VALVE 25-MOV-2531 | TECHNOR | CPSG-26/EFSRC-420 | 20P0092450020 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 987 | Ashik Kasim | 2023-08-07 09:38 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
988 | 9D63AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6181947,24.9744924 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-2531 | CD_25-MOV-2531 | MOV - LP SUCTION HEADER-COMMON TO MEC 3 | BIFFI | WGR3200 + ICON-020/180-144 (3000 Series) | 192273E0013001 | Electrical | Not Available | Gb | IEC | Ex d. h ia | IIB | T4 | IP66/68 | -20 +85 | INE | IECEx INE 18.0026X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 988 | Ashik Kasim | 2023-08-07 09:41 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
989 | 22C3AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6181615,24.9745218 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-2582 | CD_25-XY-2582 | SOLENOID VALVE, SHUTDOWN VALVE 25-MOV-2532 BYPASS LINE | Bifold | FP06P-77A | FL10919-8385 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 989 | Ashik Kasim | 2023-08-07 09:49 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
990 | 1AC1AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6181804,24.9745778 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZSO-2582/25-ZSC-2582 | CD_25-ZS-2582 | POSITION SWITCH , SHUTDOWN VALVE 25-MOV-2532 BYPASS LINE | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 990 | Ashik Kasim | 2023-08-07 09:52 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
991 | E3BFAB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6181306,24.9745354 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PDIT-2532 | CA_25-PDIT-2532 | DP TRANSMITTER, 25-XV-2582 | Rosemount | 300S1AAD1E7M5 | 942291 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T5 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 991 | Ashik Kasim | 2023-08-08 05:39 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
992 | 62C1AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6181898,24.9744973 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-300 | CD_25-XY-300 | SOLENOID VALVE, SHUTDOWN VALVE INLET MEC-3 (25-C-203/203) | Bifold | FP06P-77A | FL10919-0366 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 992 | Ashik Kasim | 2023-08-08 05:43 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
993 | FF5AAB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.618133,24.9744635 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZSO-300/25-ZSC-300 | CD_25-ZS-300 | POSITION SWITCH CLOSED, SHUTDOWN VALVE INLET MEC-3 (25-C-203/203) | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 993 | Ashik Kasim | 2023-08-08 05:46 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
994 | F4C0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179646,24.9744935 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FIT-302A | CA_25-FIT-302A | FLOW TRANSMITTER, MULTI ENVELOPE COMPRESSOR 3 - HP SECTION | Rosemount | Not Available | 0500187 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 09.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 994 | Ashik Kasim | 2023-08-08 06:03 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
995 | 60C2AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6180561,24.9745013 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-316-ISO | 25-PC-112A | ISOLATOR, MOTOR OPERATED VALVE 25-MOV-316 | TECHNOR | CPSG-26/EFSRC-420 | 20P0092450021 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 995 | Ashik Kasim | 2023-08-08 05:57 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
996 | 58C4AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6180374,24.9744383 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-316 | CD_25-MOV-316 | MOV - 25-C-302 HP SECTION INLET | BIFFI | WGR3200 + ICON-020/180-144 (3000 Series) | 192273E003001 | Electrical | Not Available | Gb | IEC | Ex d. h ia | IIB | T4 | IP66/68 | -20 +85 | INE | IECEx INE 18.0026X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 996 | Ashik Kasim | 2023-08-08 05:59 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
997 | 2BC0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179467,24.9745328 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FIT-302B | CA_25-FIT-302B | FLOW TRANSMITTER, MULTI ENVELOPE COMPRESSOR 3 - HP SECTION | Rosemount | Not Available | 0942627 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 09.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 997 | Ashik Kasim | 2023-08-08 06:05 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
998 | F5C3AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179467,24.9745328 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FIT-301A | CA_25-FIT-301A | FLOW TRANSMITTER, MULTI ENVELOPE COMPRESSOR 3 - LP SECTION | Rosemount | Not Available | 0500186 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 09.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 998 | Ashik Kasim | 2023-08-08 06:08 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
999 | F9C1AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179514,24.9744891 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FIT-301B | CA_25-FIT-301B | FLOW TRANSMITTER, MULTI ENVELOPE COMPRESSOR 3 - LP SECTION | Rosemount | Not Available | 0500192 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 09.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 999 | Ashik Kasim | 2023-08-08 06:10 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1000 | B0BEAB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.617945,24.9745136 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-303 | CA_25-TIT-303 | TEMPERATURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 3 - HP SECTION | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 0944305 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1000 | Ashik Kasim | 2023-08-08 06:14 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1001 | 9EC1AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179156,24.9744918 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-301 | CA_25-TIT-301 | TEMPERATURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 3 - LP SECTION | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 03587956 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1001 | Ashik Kasim | 2023-08-08 06:19 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1002 | 93C3AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179081,24.9745066 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PDIT-301 | CA_25-PDIT-301 | DP TRANSMITTER, 25-C-301 LP SECTION INLET FILTER | Rosemount | 3051S1CD3A2A11A1AC5D1E7Y2M5P1Q4Q8QTQ15 | 942301 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T5 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1002 | Ashik Kasim | 2023-08-08 06:25 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1003 | 52C1AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179556,24.9745152 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PDIT-302 | CA_25-PDIT-302 | DP TRANSMITTER, 25-C-302 LP SECTION INLET FILTER | Rosemount | 3051S1CD3A2A11A1AC5D1E7Y2M5P1Q4Q8QTQ15 | 942302 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T5 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1003 | Ashik Kasim | 2023-08-08 06:27 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1004 | B7C0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179463,24.9747337 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-309 | CA_25-PIT-309 | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 3 - HP SECTION | Rosemount | Not visible | 941221 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1004 | Ashik Kasim | 2023-08-08 06:32 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1005 | 7263AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6178934,24.9745198 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-308 | CA_25-PIT-308 | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 3 - HP SECTION | Rosemount | Not visible | 942210 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1005 | Ashik Kasim | 2023-08-08 06:33 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1006 | EBC4AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6178743,24.9744937 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-303 | CA_25-PIT-303 | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 3 - HP SECTION | Rosemount | 3051TG4A2B21BWR3B4E7D4M5Q4Q8S5QT | 0500059 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 09.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1006 | Ashik Kasim | 2023-08-08 06:36 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1007 | 5BC0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.617932,24.9744959 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-301 | CA_25-PIT-301 | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 3 - LP SECTION | Rosemount | 3051TG4A2B21BWR3B4E7D4M5Q4Q8S5QT | 0500058 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 09.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1007 | Ashik Kasim | 2023-08-08 06:40 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1008 | F6C1AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179744,24.9745091 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-305 | CD_25-XY-305 | SOLENOID VALVE, MEC 3 HOT GAS BYPASS - HP STAGE | ASCO | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex d | IIC | T6 | IP67 | -50 +60 | LCIE | IECEx LCIE07.0015X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1008 | Ashik Kasim | 2023-08-08 08:47 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1009 | 97BFAB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179705,24.9744996 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FZSC-304/25-FZSO-304 | CD_25-ZS-304 | POSITION SWITCH OPEN, MEC 3 HOT GAS BYPASS -LP STAGE | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1009 | Ashik Kasim | 2023-08-08 08:40 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1010 | 91C0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179898,24.9745473 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-304 | CD_25-XY-304 | SOLENOID VALVE, MEC 3 HOT GAS BYPASS - LP STAGE | ASCO | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex d | IIC | T6 | IP67 | -50 +60 | LCIE | IECEx LCIE07.0015X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1010 | Ashik Kasim | 2023-08-08 08:45 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1011 | 1EC5AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.618049,24.9744745 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FZSC-305/25-FZSO-305 | CD_25-ZS-305 | POSITION SWITCH OPEN, MEC 3 HOT GAS BYPASS -HP STAGE | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close | A6. Equipment id not available | A6. Fix equipment id |  | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 1011 | Ashik Kasim | 2023-08-08 11:02 | A6. Pending | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable
1012 | A1BFAB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179512,24.9745538 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2535T | CA_25-AE-2535T | FLAMMABLE GAS DETECTOR - OPEN PATH TYPE TRANSMITTER | Eye Safe | Quasar 900 | Not visible | Instrumentation | Not Applicable | Gb | IEC | Ex d | IIB + H2 | T4 | IP64 | -40 +75 | SIRA | IECEx SIR 13.0069X | Yes | Others | Periodic | d | Close | A10. Wrong type blanking elements installed | A10. Replace with suitable type blanking elements | Teflon tape used along with Stop plugs | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1012 | Ashik Kasim | 2023-08-08 11:00 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-08-28 09:26
1013 | A02BAA4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area- Ground | 55.6181796,24.9745792 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-DJBS-2531 | CD_25-DJBS-2531 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039889 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1013 | Ashik Kasim | 2023-08-08 09:58 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1014 | 7CBEAB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area- Ground | 55.6181953,24.9745651 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-DJBS-2532 | CD_25-DJBS-2532 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039929 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1014 | Ashik Kasim | 2023-08-08 09:58 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1015 | 23C0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area- Ground | 55.6182058,24.974537 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-DJBS-2531 | CD_25-DJBS-2531 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039938 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1015 | Ashik Kasim | 2023-08-08 10:07 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1016 | 41C2AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area- Ground | 55.6181178,24.9745778 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FJBD-2531 | CD_25-FJBD-2531 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039902 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1016 | Ashik Kasim | 2023-08-08 10:09 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1017 | EEBFAB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area- Ground | 55.6181355,24.9745614 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-UJBD-2532 | CD_25-UJBD-2532 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039933 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1017 | Ashik Kasim | 2023-08-08 10:12 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1018 | 38C6AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area- Ground | 55.6180491,24.9745324 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-UJBS-2533 | CD_25-UJBS-2533 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039949 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1018 | Ashik Kasim | 2023-08-08 10:15 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1019 | 5FBEAB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area- Ground | 55.617981,24.9745839 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FJBS-2531 | CD_25-FJBS-2531 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039923 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1019 | Ashik Kasim | 2023-08-08 10:19 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1020 | 8DC3AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area- Ground | 55.6178484,24.9745862 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-UJBS-2531 | CD_25-UJBS-2531 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039948 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1020 | Ashik Kasim | 2023-08-08 10:23 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1021 | 385AAB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area- Ground | 55.6181626,24.974494 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-UJBD-2531 | CD_25-UJBD-2531 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039918 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1021 | Ashik Kasim | 2023-08-08 10:27 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1022 | B2C1AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area- Ground | 55.6181648,24.9744577 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HS-2537 | CD_25-HS-2537 | MANUAL CALL POINT | EATON | SM87PBLD | 2156858197114 | Instrumentation | Not Available | Gb | IEC | Ex d | IIC | T5 | IP66/67 | -55 +70 | BAS | IECEx BAS 09.0060 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1022 | Ashik Kasim | 2023-08-08 10:32 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1023 | 5BC4AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179119,24.974481 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-307 | CA_25-PIT-307 | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 3 - LP SECTION | Rosemount | Not visible | 942218 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1023 | Ashik Kasim | 2023-08-09 05:41 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1024 | 7BBEAB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179227,24.9744886 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-305 | CA_25-PIT-305 | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 3 - LP SECTION | Rosemount | 3051TG4A2B21BWR3B4E7D4M5Q4Q8S5QT | 0500181 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 09.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1024 | Ashik Kasim | 2023-08-09 05:43 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1025 | 94C1AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.617945,24.9745136 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-307 | CA_25-TIT-307 | TEMPERATURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 3 - LP SECTION | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 03587958 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1025 | Ashik Kasim | 2023-08-09 06:15 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1026 | 09C2AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179317,24.9745276 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-302A | CA_25-PIT-302A | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 3 - LP SECTION | Rosemount | Not visible | 942207 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1026 | Ashik Kasim | 2023-08-09 05:41 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1027 | B9C4AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.617942,24.974551 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-302B | CA_25-PIT-302B | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 3 - LP SECTION | Rosemount | Not visible | 942207 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1027 | Ashik Kasim | 2023-08-09 05:41 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1028 | 88BEAB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179205,24.9744974 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-302C | CA_25-PIT-302C | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 3 - LP SECTION | Rosemount | Not visible | Not visible | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1028 | Ashik Kasim | 2023-08-09 06:20 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1029 | 4A5DAB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179306,24.9744675 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-302A | CA_25-TIT-302A | TEMPERATURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 3 - LP SECTION | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 03587977 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1029 | Ashik Kasim | 2023-08-09 06:22 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1030 | 315BAB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.617933,24.9745053 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-302B | CA_25-TIT-302B | TEMPERATURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 3 - LP SECTION | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 03587978 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1030 | Ashik Kasim | 2023-08-09 06:23 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1031 | 55C4AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179112,24.9744521 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-302C | CA_25-TIT-302C | TEMPERATURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 3 - LP SECTION | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 0944306 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1031 | Ashik Kasim | 2023-08-09 06:25 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1032 | E92BAA4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179665,24.9745159 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-304C | CA_25-TIT-304C | TEMPERATURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 3 - HP SECTION | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 3587983 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1032 | Ashik Kasim | 2023-08-09 06:28 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1033 | D2BEAB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179604,24.9745093 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-304B | CA_25-TIT-304B | TEMPERATURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 3 - HP SECTION | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 3587982 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1033 | Ashik Kasim | 2023-08-09 06:31 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1034 | BDC0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179306,24.974523 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-304A | CA_25-TIT-304A | TEMPERATURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 3 - HP SECTION | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 3587981 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1034 | Ashik Kasim | 2023-08-09 06:33 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1035 | 81BEAB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179683,24.9745098 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-304C | CA_25-PIT-304C | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 3 - HP SECTION | Rosemount | Not visible | 942214 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1035 | Ashik Kasim | 2023-08-09 06:35 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1036 | 35C0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179315,24.9744768 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-304B | CA_25-PIT-304B | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 3 - HP SECTION | Rosemount | Not visible | 942213 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1036 | Ashik Kasim | 2023-08-09 06:36 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1037 | BEC4AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179219,24.9744877 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-304A | CA_25-PIT-304A | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 3 - HP SECTION | Rosemount | Not visible | 942212 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1037 | Ashik Kasim | 2023-08-09 06:41 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1038 | B6C0AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6180248,24.9746183 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-308 | CA_25-TIT-308 | TEMPERATURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 3 - HP SECTION | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 3587980 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1038 | Ashik Kasim | 2023-08-09 09:02 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1039 | 86BEAB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6179455,24.9745033 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-306 | CA_25-PIT-306 | PRESSURE TRANSMITTER, MULTI ENVELOPE COMPRESSOR 3 - LP SECTION | Rosemount | 3051TG4A2B21BWR3B4E7D4M5Q4Q8S5QT | 0500178 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 09.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1039 | Ashik Kasim | 2023-08-09 09:08 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1040 | 5BC1AB4E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Area (+15) | 55.6181676,24.9747291 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2534 | CA_25-AE-2534 | FLAMMABLE GAS DETECTOR - IR POINT TYPE | Net Safety | SC311S-100-ASSY | 085914 | Instrumentation | Not Available | Gb | IEC | Ex d | IIB + H2 | T5 | IP64 | -40 +75 | FMG | IECExFMG 12.0007X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1040 | Ashik Kasim | 2023-08-09 09:15 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1041 | 29C0AB4E080104E0 |  | Margham | Area 25 | MEC Discharge Pipeline Area | 55.618313,24.9743883 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-2507A | CA_25-PIT-2507A | PRESSURE TRANSMITTER, DISCHARGE HEADER | Rosemount | Not visible | 942176 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1041 | Ashik Kasim | 2023-08-09 09:29 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1042 | D1BEAB4E080104E0 |  | Margham | Area 25 | MEC Discharge Pipeline Area | 55.6183254,24.9743911 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-2507B | CA_25-PIT-2507B | PRESSURE TRANSMITTER, DISCHARGE HEADER | Rosemount | Not visible | Not visible | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1042 | Ashik Kasim | 2023-08-09 09:32 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1043 | 35C2AB4E080104E0 |  | Margham | Area 25 | MEC Discharge Pipeline Area | 55.618349,24.9743886 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-2507C | CA_25-PIT-2507C | PRESSURE TRANSMITTER, DISCHARGE HEADER | Rosemount | Not visible | 942177 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1043 | Ashik Kasim | 2023-08-09 09:34 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1044 | 70C0AB4E080104E0 |  | Margham | Area 25 | MEC Discharge Pipeline Area | 55.6183723,24.9744062 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2505 | CA_25-AE-2505 | FLAMMABLE GAS DETECTOR - IR POINT TYPE | Net Safety | SC311S-100-ASSY | 085899 | Instrumentation | Not Available | Gb | IEC | Ex d | IIB + H2 | T5 | IP64 | -40 +75 | FMG | IECExFMG 12.0007X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1044 | Ashik Kasim | 2023-08-09 09:39 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1045 | CDBFAB4E080104E0 |  | Margham | Area 25 | MEC Discharge Pipeline Area | 55.6183979,24.9743528 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-2552-ISO | 25-PC-821A | ISOLATOR, MOTOR OPERATED VALVE 25-MOV-2552 | TECHNOR | CPSG-26/EFSRC-420 | 21P0141320002 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1045 | Ashik Kasim | 2023-08-09 09:44 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1046 | 4BC1AB4E080104E0 |  | Margham | Area 25 | MEC Discharge Pipeline Area | 55.6183828,24.9743684 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-2552 | CD_25-MOV-2552 | MOV - FROM MEC DISCHARGE HEADER | BIFFI | WGR3200 + ICON-020/180-144 (3000 Series) | 192273E003001 | Electrical | Not Available | Gb | IEC | Ex d. h ia | IIB | T4 | IP66/68 | -20 +85 | INE | IECEx INE 18.0026X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1046 | Ashik Kasim | 2023-08-09 09:48 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1047 | 8FC3AB4E080104E0 |  | Margham | Area 25 | MEC Discharge Pipeline Area | 55.6183638,24.9743467 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2506 | CA_25-AE-2506 | FLAMMABLE GAS DETECTOR - IR POINT TYPE | Net Safety | SC311S-100-ASSY | 085900 | Instrumentation | Not Available | Gb | IEC | Ex d | IIB + H2 | T5 | IP64 | -40 +75 | FMG | IECExFMG 12.0007X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1047 | Ashik Kasim | 2023-08-09 09:53 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1048 | 54C4AB4E080104E0 |  | Margham | Area 25 | MEC Discharge Pipeline Area | 55.6183319,24.9743752 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-2550 | CD_25-MOV-2550 | MOV - FROM MEC DISCHARGE HEADER (HP INJ. EAST) | AUMA | Not Available | 2218MD21047 | Electrical | Not Available | Gb | NEC | Class 1 Div 1 | C D | T3A | Not Available | -30 +70 | FM | Not available | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1048 | Ashik Kasim | 2023-08-09 10:04 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1049 | F3BFAB4E080104E0 |  | Margham | Area 25 | MEC Discharge Pipeline Area | 55.6183431,24.9743622 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-2550-ISO | 25-PC-127A | ISOLATOR, MOTOR OPERATED VALVE 25-MOV-2550 | TECHNOR | CPSG-26/EFSRC-420 | 21P0092450019 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1049 | Ashik Kasim | 2023-08-09 10:09 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1050 | 22C4AB4E080104E0 |  | Margham | Area 25 | MEC Discharge Pipeline Area | 55.6183283,24.9743539 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-2551 | CD_25-MOV-2551 | MOV - FROM MEC DISCHARGE HEADER (HP INJ. WEST) | AUMA | Not Available | 2218MD21048 | Electrical | Not Available | Gb | NEC | Class 1 Div 1 | C D | T3A | Not Available | -30 +70 | FM | Not available | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1050 | Ashik Kasim | 2023-08-09 10:14 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1051 | E8C3AB4E080104E0 |  | Margham | Area 25 | MEC Discharge Pipeline Area | 55.618343,24.9743456 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-MOV-2551-ISO | 25-PC-128B | ISOLATOR, MOTOR OPERATED VALVE 25-MOV-2551 | TECHNOR | CPSG-26/EFSRC-420 | 21P0092450017 | Electrical | 2 | Gb | IEC | Ex db | IIC | T6 | IP66 | -20 +50 | INERIS | INERIS 03ATEX0009X | Yes | Motor | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1051 | Ashik Kasim | 2023-08-09 10:18 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1052 | 71C0AB4E080104E0 |  | Margham | Area 25 | MEC Pipeline Suction Area | 55.6180728,24.9754351 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2502 | CA_25-AE-2502 | FLAMMABLE GAS DETECTOR - IR POINT TYPE | Net Safety | SC311S-100-ASSY | 085896 | Instrumentation | Not Available | Gb | IEC | Ex d | IIB + H2 | T5 | IP64 | -40 +75 | FMG | IECExFMG 12.0007X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1052 | Ashik Kasim | 2023-08-10 05:48 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1053 | 84C3AB4E080104E0 |  | Margham | Area 25 | MEC Pipeline Suction Area | 55.6180731,24.975453 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2503 | CA_25-AE-2503 | FLAMMABLE GAS DETECTOR - IR POINT TYPE | Net Safety | SC311S-100-ASSY | 085895 | Instrumentation | Not Available | Gb | IEC | Ex d | IIB + H2 | T5 | IP64 | -40 +75 | FMG | IECExFMG 12.0007X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1053 | Ashik Kasim | 2023-08-10 05:49 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1054 | F2C3AB4E080104E0 |  | Margham | Area 25 | MEC Pipeline Suction Area | 55.618048,24.9754197 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FIT-2501 | CA_25-FIT-2501 | FLOW TRANSMITTER, LP SUCTION HEADER | Rosemount | Not Available | 0942626 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 09.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1054 | Ashik Kasim | 2023-08-10 05:47 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1055 | C7C1AB4E080104E0 |  | Margham | Area 25 | MEC Pipeline Suction Area | 55.6180906,24.9754397 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-2501 | CA_25-PIT-2501 | PRESSURE TRANSMITTER, LP SUCTION HEADER | Rosemount | Not visible | 942169 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1055 | Ashik Kasim | 2023-08-10 05:53 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1056 | F4C3AB4E080104E0 |  | Margham | Area 25 | MEC Pipeline Suction Area | 55.618048,24.9754614 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-2501 | CA_25-TIT-2501 | TEMPERATURE TRANSMITTER, LP SUCTION HEADER | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 3588021 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1056 | Ashik Kasim | 2023-08-10 05:58 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1057 | 21C3AB4E080104E0 |  | Margham | Area 25 | MEC Pipeline Suction Area | 55.6181143,24.9754402 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-2503 | CD_25-XY-2503 | SOLENOID VALVE, SHUTDOWN VALVE LP SUCTION HEADER | Bifold | FP06P-77A | FL10919-0389 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1057 | Ashik Kasim | 2023-08-10 06:01 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1058 | 5AC2AB4E080104E0 |  | Margham | Area 25 | MEC Pipeline Suction Area | 55.6181153,24.975463 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZSO-2503/25-ZSC-2503 | CD_25-ZS-2503 | POSITION SWITCH , SHUTDOWN VALVE LP SUCTION HEADER | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1058 | Ashik Kasim | 2023-08-10 06:06 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1059 | 9FC0AB4E080104E0 |  | Margham | Area 25 | MEC Pipeline Suction Area | 55.6181263,24.9754053 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2504 | CA_25-AE-2504 | FLAMMABLE GAS DETECTOR - IR POINT TYPE | Net Safety | SC311S-100-ASSY | 085898 | Instrumentation | Not Available | Gb | IEC | Ex d | IIB + H2 | T5 | IP64 | -40 +75 | FMG | IECExFMG 12.0007X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1059 | Ashik Kasim | 2023-08-10 06:07 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1060 | 90C3AB4E080104E0 |  | Margham | Area 25 | MEC Pipeline Suction Area | 55.6181458,24.9754441 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-2505 | CA_25-PIT-2505 | PRESSURE TRANSMITTER, LP SUCTION HEADER | Rosemount | Not visible | 942170 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1060 | Ashik Kasim | 2023-08-10 06:12 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1061 | 6BC0AB4E080104E0 |  | Margham | Area 25 | MEC Pipeline Suction Area | 55.6181982,24.9754366 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-2503 | CA_25-PIT-2503 | PRESSURE TRANSMITTER, LP SUCTION HEADER | Rosemount | Not visible | 942171 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1061 | Ashik Kasim | 2023-08-10 06:16 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1062 | 67C0AB4E080104E0 |  | Margham | Area 25 | MEC Pipeline Suction Area | 55.6181931,24.9754131 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-DJBD-2501 | CD_25-DJBD-2501 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039903 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1062 | Ashik Kasim | 2023-08-10 06:21 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1063 | 9BC0AB4E080104E0 |  | Margham | Area 25 | MEC Pipeline Suction Area | 55.6181784,24.9753904 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-DJBS-2501 | CD_25-DJBS-2501 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039893 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1063 | Ashik Kasim | 2023-08-10 06:21 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1064 | BEC0AB4E080104E0 |  | Margham | Area 25 | MEC Pipeline Suction Area | 55.6182303,24.9754406 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FJBS-2501 | CD_25-FJBS-2501 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039911 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1064 | Ashik Kasim | 2023-08-10 06:24 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1065 | CCC1AB4E080104E0 |  | Margham | Area 25 | MEC Pipeline Suction Area | 55.618221,24.9753906 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-EJBD-2501 | CD_25-EJBD-2501 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039879 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1065 | Ashik Kasim | 2023-08-10 06:26 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1066 | D7C5AB4E080104E0 |  | Margham | Area 25 | MEC Pipeline Suction Area | 55.6181698,24.975362 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-EJBS-2501 | CD_25-EJBS-2501 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039884 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1066 | Ashik Kasim | 2023-08-10 06:33 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1067 | 6DC1AB4E080104E0 |  | Margham | Area 25 | MEC Pipeline Suction Area | 55.6180388,24.975447 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-2504 | CD_25-XY-2504 | SOLENOID VALVE, SHUTDOWN VALVE HP SUCTION HEADER | Bifold | FP06P-77A | FL10919-0392 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1067 | Ashik Kasim | 2023-08-10 06:35 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1068 | 377AAB4E080104E0 |  | Margham | Area 25 | MEC Pipeline Suction Area | 55.618055,24.9754672 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZSO-2504/25-ZSC-2504 | CD_25-ZS-2504 | POSITION SWITCH , SHUTDOWN VALVE HP SUCTION HEADER | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1068 | Ashik Kasim | 2023-08-10 06:38 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1069 | E6C4AB4E080104E0 |  | Margham | Area 25 | MEC Pipeline Suction Area | 55.6179427,24.9754375 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2501 | CA_25-AE-2501 | FLAMMABLE GAS DETECTOR - IR POINT TYPE | Net Safety | SC311S-100-ASSY | 085895 | Instrumentation | Not Available | Gb | IEC | Ex d | IIB + H2 | T5 | IP64 | -40 +75 | FMG | IECExFMG 12.0007X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1069 | Ashik Kasim | 2023-08-10 06:42 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1070 | E1C0AB4E080104E0 |  | Margham | Area 25 | MEC Pipeline Suction Area | 55.6182321,24.9754868 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-2507 | CD_25-XY-2507 | SOLENOID VALVE, SHUTDOWN VALVE HP SUCTION HEADER | Bifold | FP06P-77A | FL10919-0364 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1070 | Ashik Kasim | 2023-08-10 08:13 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1071 | DEBEAB4E080104E0 |  | Margham | Area 25 | MEC Pipeline Suction Area | 55.6182021,24.9754803 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZSO-2507/25-ZSC-2507 | CD_25-ZS-2507 | POSITION SWITCH , SHUTDOWN VALVE HP SUCTION HEADER | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1071 | Ashik Kasim | 2023-08-10 08:15 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1072 | 145EAB4E080104E0 |  | Margham | Area 25 | MEC Pipeline Suction Area | 55.6182275,24.9755047 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XY-2508 | CD_25-XY-2508 | SOLENOID VALVE, SHUTDOWN VALVE HP SUCTION HEADER | Bifold | FP06P-77A | FL10919-0371 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP67 | -60 +55 | Baseefa | Baseefa10ATEX0026 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1072 | Ashik Kasim | 2023-08-10 08:24 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1073 | 87C1AB4E080104E0 |  | Margham | Area 25 | MEC Pipeline Suction Area | 55.6181384,24.9754811 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZSO-2508/25-ZSC-2508 | CD_25-ZS-2508 | POSITION SWITCH , SHUTDOWN VALVE HP SUCTION HEADER | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1073 | Ashik Kasim | 2023-08-10 08:26 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1074 | 50C4AB4E080104E0 |  | Margham | Area 25 | MEC Pipeline Suction Area | 55.6180475,24.9754698 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-2506 | CA_25-PIT-2506 | PRESSURE TRANSMITTER, HP SUCTION HEADER | Rosemount | Not visible | 942173 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1074 | Ashik Kasim | 2023-08-10 08:34 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1075 | BEC2AB4E080104E0 |  | Margham | Area 25 | MEC Pipeline Suction Area | 55.6180394,24.97545 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-2504 | CA_25-PIT-2504 | PRESSURE TRANSMITTER, HP SUCTION HEADER | Rosemount | Not visible | 942174 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1075 | Ashik Kasim | 2023-08-10 08:38 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1076 | C4C1AB4E080104E0 |  | Margham | Area 25 | MEC Pipeline Suction Area | 55.6179777,24.9754449 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FIT-2502 | CA_25-FIT-2502 | FLOW TRANSMITTER, HP SUCTION HEADER | Rosemount | Not Available | 0942622 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 09.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1076 | Ashik Kasim | 2023-08-10 08:45 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1077 | C5BEAB4E080104E0 |  | Margham | Area 25 | MEC Pipeline Suction Area | 55.6179939,24.9754523 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-2502 | CA_25-PIT-2502 | PRESSURE TRANSMITTER, HP SUCTION HEADER | Rosemount | Not visible | 942172 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1077 | Ashik Kasim | 2023-08-10 08:50 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1078 | 2A5CAB4E080104E0 |  | Margham | Area 25 | MEC Pipeline Suction Area | 55.6179682,24.9754427 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-2502 | CA_25-TIT-2502 | TEMPERATURE TRANSMITTER, HP SUCTION HEADER | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 3587937 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1078 | Ashik Kasim | 2023-08-10 08:57 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1079 | 85C1AB4E080104E0 |  | Margham | Area 25 | MEC-Substation Front Side | 55.617692,24.9751775 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FJBD-2502 | CD_25-FJBD-2502 | INSTRUMENT JB | Weidmuller | MH453820S4N1 | XB-AE-A-039898 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T5 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1079 | Ashik Kasim | 2023-08-10 09:21 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1080 | 23C4AB4E080104E0 |  | Margham | Area 25 | MEC-Substation Front Side | 55.6176816,24.9752104 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HS-2542 | CD_25-HS-2542 | MANUAL CALL POINT | EATON | SM87PBLD | 2156858197103 | Instrumentation | Not Available | Gb | IEC | Ex d | IIC | T5 | IP66/67 | -55 +70 | BAS | IECEx BAS 09.0060 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1080 | Ashik Kasim | 2023-08-10 09:24 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1081 | C8C1AB4E080104E0 |  | Margham | Area 25 | MEC-Substation Front Side | 55.617684,24.9752101 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XA-2502G | CD_25-XA-2502G | SINGLE TONE SOUNDER (WITH ADJUSTABLE TONE & VOLUME) | EATON | DB3BG | 215685819 91 01 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T4 | Not Available | -55 +85 | Baseefa | Baseefa13ATEX0229X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1081 | Ashik Kasim | 2023-08-10 09:31 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1082 | ECC4AB4E080104E0 |  | Margham | Area 25 | MEC-Substation Front Side | 55.6176403,24.9752417 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XA-2502F | CD_25-XA-2502F | SINGLE TONE SOUNDER (WITH ADJUSTABLE TONE & VOLUME) | EATON | DB3BG | 215685819 61 02 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T4 | Not Available | -55 +85 | Baseefa | Baseefa13ATEX0229X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1082 | Ashik Kasim | 2023-08-10 09:35 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1083 | 1FC5AB4E080104E0 |  | Margham | Area 25 | MEC-Substation Front Side | 55.6176221,24.9752832 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XL-2502G | CD_25-XL-2502G | FLASHING BEACON (WITH RED GLASS FOR FIRE & BLUE GLASS FOR GAS) | EATON | XB4 | 2156958195102 | Instrumentation | Not Available | Gb | IEC | Ex d | IIC | T4 | IP65 | -55 +60 | BAS | IECExBAS10.0078X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1083 | Ashik Kasim | 2023-08-10 09:37 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1084 | F7C1AB4E080104E0 |  | Margham | Area 25 | MEC-Substation Front Side | 55.6176515,24.975254 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XL-2502F | CD_25-XL-2502F | FLASHING BEACON (WITH RED GLASS FOR FIRE & BLUE GLASS FOR FIRE | EATON | XB4 | 215695819 41 02 | Instrumentation | Not Available | Gb | IEC | Ex d | IIC | T4 | IP65 | -55 +60 | BAS | IECExBAS10.0078X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1084 | Ashik Kasim | 2023-08-10 09:39 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1085 | C3C1AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.6178505,24.9752619 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HS-2516 | CD_25-HS-2516 | MANUAL CALL POINT | EATON | SM87PBLD | 2156858197105 | Instrumentation | Not Available | Gb | IEC | Ex d | IIC | T5 | IP66/67 | -55 +70 | BAS | IECEx BAS 09.0060 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1085 | Ashik Kasim | 2023-08-11 05:35 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1086 | D4C1AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.6178466,24.9752592 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2502 | CA_25-AE-2502 | FLAMMABLE GAS DETECTOR - IR POINT TYPE | Net Safety | SC311S-100-ASSY | 085901 | Instrumentation | Not Available | Gb | IEC | Ex d | IIB + H2 | T5 | IP64 | -40 +75 | FMG | IECExFMG 12.0007X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1086 | Ashik Kasim | 2023-08-11 05:38 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1087 | 9B5AAB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.6179322,24.9752357 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-124 | 25-PIT-124 | PRESSURE TRANSMITTER, COOLING GAS SYSTEM COMPRESSOR-A | Rosemount | Not visible | 0500054 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1087 | Ashik Kasim | 2023-08-11 05:45 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1088 | 89BFAB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.6179218,24.9751563 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-125 | 25-PIT-125 | PRESSURE TRANSMITTER, COOLING GAS SYSTEM COMPRESSOR-A | Rosemount | Not visible | 0500194 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1088 | Ashik Kasim | 2023-08-11 05:46 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1089 | 3CC0AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.618045,24.9750628 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TE-126 | 25-TE-126 | RTD, COOLING GAS SYSTEM COMPRESSOR-A | Rosemount | 0065CN1N0000N0245E7TB | 050064437 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T5 | Not Available | -50 +80 | FMG | IECExFMG12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1089 | Ashik Kasim | 2023-08-11 06:01 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1090 | 3BC0AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.6180574,24.9751288 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TE-127 | 25-TE-127 | RTD, COOLING GAS SYSTEM COMPRESSOR-A | Rosemount | 0065CN1N0000N0245E7TB | 050064438 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T5 | Not Available | -50 +80 | FMG | IECExFMG12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1090 | Ashik Kasim | 2023-08-11 06:00 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1091 | E62BAA4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.6180676,24.9751259 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-126 | 25-PIT-126 | PRESSURE TRANSMITTER, COOLING GAS SYSTEM COMPRESSOR-A | Rosemount | Not visible | 0500195 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1091 | Ashik Kasim | 2023-08-11 06:02 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1092 | DCC1AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.6180575,24.9751592 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2512 | CA_25-AE-2512 | FLAMMABLE GAS DETECTOR - IR POINT TYPE | Net Safety | SC311S-100-ASSY | 085902 | Instrumentation | Not Available | Gb | IEC | Ex d | IIB + H2 | T5 | IP64 | -40 +75 | FMG | IECExFMG 12.0007X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1092 | Ashik Kasim | 2023-08-11 06:08 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1093 | D15EAB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.618034,24.9752645 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-131 | 25-PIT-131 | PRESSURE TRANSMITTER, COOLING GAS SYSTEM COMPRESSOR-A | Rosemount | Not visible | 0500061 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1093 | Ashik Kasim | 2023-08-11 06:11 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1094 | F7BFAB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.6179977,24.9752942 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-125 | CA_25-TIT-125 | TEMPERATURE TRANSMITTER, COOLING GAS SYSTEM COMPRESSOR-A | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 5123898 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1094 | Ashik Kasim | 2023-08-11 06:15 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1095 | BDC3AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.617967,24.9751853 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-127 | 25-PIT-127 | PRESSURE TRANSMITTER, COOLING GAS SYSTEM COMPRESSOR-A | Rosemount | Not visible | 0500200 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1095 | Ashik Kasim | 2023-08-11 06:17 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1096 | 25C4AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.6179806,24.9751724 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-128 | 25-PIT-128 | PRESSURE TRANSMITTER, COOLING GAS SYSTEM COMPRESSOR-A | Rosemount | Not visible | 0500201 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1096 | Ashik Kasim | 2023-08-11 06:21 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1097 | 98C1AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.6181306,24.9745354 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PDIT-123 | CA_25-PDIT-123 | DP TRANSMITTER, COOLING GAS | Rosemount | 3051CD3A02A1BWR3SE7M5Q4Q8QTD4 | 0500210 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T5 | IP66/68 | -20 +85 | BAS | IECEx BAS 10.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1097 | Ashik Kasim | 2023-08-11 06:31 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1098 | EDC1AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.6180627,24.9752247 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZT-121 | 25-ZT-121 | POSITION TRANSMITTER, TEMPERATURE CONTROL VALVE COOLING GAS | FISHER | DVC6200 | F002086252 | Instrumentation | Not Available | Ga | IEC | Ex d ia | IIC | T5 | IP66/68 | -40 +80 | CSA | IECExCSA16.0003X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1098 | Ashik Kasim | 2023-08-11 08:48 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1099 | 65C2AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.6180449,24.9752028 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZT-123 | 25-ZT-123 | POSITION TRANSMITTER, TEMPERATURE CONTROL VALVE COOLING GAS | FISHER | DVC6200 | F002086256 | Instrumentation | Not Available | Ga | IEC | Ex d ia | IIC | T5 | IP66/68 | -40 +80 | CSA | IECExCSA16.0003X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1099 | Ashik Kasim | 2023-08-11 08:51 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1100 | 99C1AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.618029,24.9752322 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZT-122 | 25-ZT-122 | POSITION TRANSMITTER, TEMPERATURE CONTROL VALVE COOLING GAS | FISHER | DVC6200 | F002086252 | Instrumentation | Not Available | Ga | IEC | Ex d ia | IIC | T5 | IP66/68 | -40 +80 | CSA | IECExCSA16.0003X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1100 | Ashik Kasim | 2023-08-11 08:54 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1101 | 17C5AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.6179742,24.975253 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-GT-123A | 25-GT-123A | GAS DETECTOR TRANSMITTER | MSA | UltimaX5000 | 000100000128001B | Instrumentation | 2 | Gb | IEC | Ex d | IIC | T5 | Not Available | -40 +60 | SIRA | IECEX SIR17.0017X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1101 | Ashik Kasim | 2023-08-11 09:21 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1102 | C6BEAB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.617991,24.9751751 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-GT-123B | 25-GT-123B | GAS DETECTOR TRANSMITTER | MSA | UltimaX5000 | 0001000001280010 | Instrumentation | 2 | Gb | IEC | Ex d | IIC | T5 | Not Available | -40 +60 | SIRA | IECEX SIR17.0017X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1102 | Ashik Kasim | 2023-08-11 09:25 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1103 | 53BEAB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.6180385,24.9753288 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-GT-122B | 25-GT-122B | GAS DETECTOR TRANSMITTER | MSA | UltimaX5000 | 0001000001280012 | Instrumentation | 2 | Gb | IEC | Ex d | IIC | T5 | Not Available | -40 +60 | SIRA | IECEX SIR17.0017X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1103 | Ashik Kasim | 2023-08-11 09:28 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1104 | 77C0AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.6180171,24.9752763 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-GT-122A | 25-GT-122A | GAS DETECTOR TRANSMITTER | MSA | UltimaX5000 | 000100000128000E | Instrumentation | 2 | Gb | IEC | Ex d | IIC | T5 | Not Available | -40 +60 | SIRA | IECEX SIR17.0017X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1104 | Ashik Kasim | 2023-08-11 09:31 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1105 | 33C2AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.6180034,24.9752858 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-EJB-121 | 25-MPC-19A | Ex d - Junction Box | General Electric | E2B 760-1100-300 | 18A008-001 | Electrical | 2 | Gb | IEC | Ex d | IIC | T4 | Not Available | -30 +60 | INE | IECExINE190019X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1105 | Ashik Kasim | 2023-08-11 09:44 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1106 | F4C2AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.6180304,24.9752759 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IJB-121 | CD_25-IJB-121 | Junction Box IS | Technor | Not available | 19/00179 | Instrumentation | Not Available | Gb | IEC | Ex ia | IIC | T6 | IP66 | 0 +60 | IMQ | IECExIMQ15.0002X | Yes | Others | Periodic | i | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1106 | Ashik Kasim | 2023-08-11 09:53 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1107 | F2C1AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.6180096,24.9751474 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-JB-126 | CA _25-JB-126 | Junction Box | STAHIL | 8150/1-0600-600-150-3321 | Not available | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T4 | IP66 | -50 +60 | PTB | IECExPTB09.0048 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1107 | Ashik Kasim | 2023-08-11 10:11 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1108 | 8BC3AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.618047,24.9754066 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-JB-125 | CA _25-JB-125 | Junction Box | STAHIL | 8150/1-0400-400-150-3321 | Not available | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T4 | IP66 | -50 +60 | PTB | IECExPTB09.0048 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1108 | Ashik Kasim | 2023-08-11 10:19 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1109 | 3AC0AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.61807,24.9752695 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PBESD-121 | CD_25-PBESD-121 | ESD 3 MEC-1 SHUTDOWN MEC-1 SKID | STAHIL | 8150/5-0176-0116-091-3311 | Not available | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T4 | IP66 | -60 +60 | PTB | IECExPTB09.0049 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1109 | Ashik Kasim | 2023-08-11 10:26 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1110 | C1BFAB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.6179941,24.975283 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-EJB-122 | 25-MPC-10A | Ex e - Junction Box | General Electric | E2B 1200x970x600 | 18A008-001 | Electrical | 2 | Gb | IEC | Ex eb | IIC | T4 | Not Available | -30 +60 | INE | IECExINE190019X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1110 | Ashik Kasim | 2023-08-11 10:49 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1111 | 115EAB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.6179139,24.9752195 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-124 | 25-TIT-124 | TEMPERATURE TRANSMITTER, COOLING GAS SYSTEM COMPRESSOR-A | Rosemount | 3144P | 5123889 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1111 | Ashik Kasim | 2023-08-11 10:41 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1112 | 55C0AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.6179406,24.9752651 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PDIT-124 | CA_25-PDIT-124 | DP TRANSMITTER, COOLING GAS | Rosemount | 3051CD3A02A1BWR3SE7M5Q4Q8QTD4 | 0500211 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T5 | IP66/68 | -20 +85 | BAS | IECEx BAS 10.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1112 | Ashik Kasim | 2023-08-11 10:43 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1113 | FBC2AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.6179315,24.975315 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-JB-124 | CA_25-JB-124-01 | Ex e - Junction Box | General Electric | E2B 800-1000-300 | 18A008-001 | Electrical | 2 | Gb | IEC | Ex eb | IIC | T4 | Not Available | -30 +60 | INE | IECExINE190019X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1113 | Ashik Kasim | 2023-08-11 10:48 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1114 | AFBFAB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.6179373,24.9752826 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-JB-123 | 25-PC-761 | Ex e - Junction Box | General Electric | E2B 800-1000-300 | 18A008-001 | Electrical | 2 | Gb | IEC | Ex eb | IIC | T4 | Not Available | -30 +60 | INE | IECExINE190019X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1114 | Ashik Kasim | 2023-08-11 10:51 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1115 | 7EBFAB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.6179122,24.9752576 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-126 | 25-TIT-126 | TEMPERATURE TRANSMITTER, COOLING GAS SYSTEM COMPRESSOR-A | Rosemount | 3144P | 5123890 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1115 | Ashik Kasim | 2023-08-11 10:54 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1116 | 21C1AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.6179236,24.9752812 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-127 | 25-TIT-127 | TEMPERATURE TRANSMITTER, COOLING GAS SYSTEM COMPRESSOR-A | Rosemount | 3144P | 5123891 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1116 | Ashik Kasim | 2023-08-11 10:58 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1117 | 8EC0AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.6179194,24.9751708 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TE-124 | 25-TE-124 | RTD, COOLING GAS SYSTEM COMPRESSOR-A | Rosemount | 0065CN1N0000N0245E7TB | 05064331 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T5 | Not Available | -50 +80 | FMG | IECExFMG12.0022X | Yes | Others | Periodic | d | Close | A6. Equipment id not available | A6. Fix equipment id |  | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 1117 | Ashik Kasim | 2023-08-11 11:11 | A6. Pending | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable
1118 | d9beab4e080104e0 |  | Margham | Area 25 | MEC-Compressor B | 24.9750614,55.6178023 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2521 | CA_25-AE-2521 | FLAMMABLE GAS DETECTOR - IR POINT TYPE | Net Safety | 0085906 | SC311S-100-ASSY | Instrumentation | Not available | Gb | IEC | Ex d | IIB+H2 | T5 | IP64 | -40 +75 | FMG | IECExFMG12.0007X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1118 | Ashik Kasim | 2023-08-14 06:00 |  |  |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1119 | 89beab4e080104e0 |  | Margham | Area 25 | MEC-Compressor B | 24.9750125,55.6178989 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-224 | 25-PIT-224 | PRESSURE TRANSMITTER, COOLING GAS SYSTEM COMPRESSOR-B | Rosemount | Not visible | 0500057 | Instrumentation | Not available | Ga | IEC | Ex d | IIC | T6 | IP66/68 | -60 +70 | KEM | IECExKEM09.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1119 | Ashik Kasim | 2023-08-14 06:06 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1120 | 82c1ab4e080104e0 |  | Margham | Area 25 | MEC-Compressor B | 24.9748024,55.6177768 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-225 | 25-PIT-225 | PRESSURE TRANSMITTER, COOLING GAS SYSTEM COMPRESSOR-B | Rosemount | Not visible | 0500196 | Instrumentation | Not available | Ga | IEC | Ex d | IIC | T6 | IP66/68 | -60 +70 | KEM | IECExKEM09.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1120 | Ashik Kasim | 2023-08-14 06:15 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1121 | ebc3ab4e080104e0 |  | Margham | Area 25 | MEC-Compressor B | 24.9748853,55.6180058 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TE-226 | 25-TE-226 | RTD, COOLING GAS SYSTEM COMPRESSOR-B | Rosemount | 0065C31N0000N0245E7TB | 05064439 | Instrumentation | Not available | Gb | IEC | Ex d | IIC | T5 | Not available | -50 +80 | FMG | IECExFMG12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1121 | Ashik Kasim | 2023-08-14 06:23 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1122 | d5c0ab4e080104e0 |  | Margham | Area 25 | MEC-Compressor B | 24.9749376,55.617999 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TE-227 | 25-TE-227 | RTD, COOLING GAS SYSTEM COMPRESSOR-B | Rosemount | 0065C31N0000N0245E7TB | 5064440 | Instrumentation | Not available | Gb | IEC | Ex d | IIC | T5 | Not available | -50 +80 | FMG | IECExFMG12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1122 | Ashik Kasim | 2023-08-14 06:35 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1123 | 0fc6ab4e080104e0 |  | Margham | Area 25 | MEC-Compressor B | 24.9747525,55.6180765 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-226 | 25-PIT-226 | PRESSURE TRANSMITTER, COOLING GAS SYSTEM COMPRESSOR-B | Rosemount | Not visible | 0500197 | Instrumentation | Not available | Ga | IEC | Ex d | IIC | T6 | IP66/68 | -60 +70 | KEM | IECExKEM09.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1123 | Ashik Kasim | 2023-08-14 08:13 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1124 | 73c0ab4e080104e0 |  | Margham | Area 25 | MEC-Compressor B | 24.9748703,55.6180496 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2522 | CA_25-AE-2522 | FLAMMABLE GAS DETECTOR - IR POINT TYPE | Net Safety | SC3119-100-ASSY | 085907 | Instrumentation | Not available | Gb | IEC | Ex d | IIB+H2 | T5 | IP64 | -40 +75 | FMG | IECExFMG12.0007X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1124 | Ashik Kasim | 2023-08-14 08:19 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1125 | 7ac0ab4e080104e0 |  | Margham | Area 25 | MEC-Compressor B | 24.9749399,55.6180008 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-231 | 25-PIT-231 | PRESSURE TRANSMITTER, COOLING GAS SYSTEM COMPRESSOR-B | Rosemount | Not visible | 0500062 | Instrumentation | Not available | Gb | IEC | Ex d | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1125 | Ashik Kasim | 2023-08-14 08:24 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1126 | 00c1ab4e080104e0 |  | Margham | Area 25 | MEC-Compressor B | 24.9749433,55.618008 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-225 | 25-TIT-225 | TEMPERATURE TRANSMITTER, COOLING GAS SYSTEM COMPRESSOR-B | Rosemount | 3144P | 5123899 | Instrumentation | Not available | Gb | IEC | Ex d | IIC | T5 | IP66 | -50 +60 | FMG | IECExFGM12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1126 | Ashik Kasim | 2023-08-14 08:29 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1127 | 91beab4e080104e0 |  | Margham | Area 25 | MEC-Compressor B | 24.9748273,55.6181048 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-227 | 25-PIT-227 | PRESSURE TRANSMITTER, COOLING GAS SYSTEM COMPRESSOR-B | Rosemount | Not visible | 0500202 | Instrumentation | Not available | Ga | IEC | Ex d | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1127 | Ashik Kasim | 2023-08-14 08:36 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1128 | 72c0ab4e080104e0 |  | Margham | Area 25 | MEC-Compressor B | 24.9747845,55.6180875 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-228 | 25-PIT-228 | PRESSURE TRANSMITTER, COOLING GAS SYSTEM COMPRESSOR-B | Rosemount | Not visible | 0500203 | Instrumentation | Not available | Ga | IEC | Ex d | IIC | T5 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1128 | Ashik Kasim | 2023-08-14 08:42 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1129 | 1dc1ab4e080104e0 |  | Margham | Area 25 | MEC-Compressor B | 24.9749138,55.6180293 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PDIT-223 | 25-PDIT-223 | DP TRANSMITTER, COOLING GAS | Rosemount | 3051CD3A02A1BWR3SE7M5Q4Q8QTD4 | 0500212 | Instrumentation | Not available | Ga | IEC | Ex db | IIC | T5 | IP66/68 | -20 +85 | BAS | IECEx BAS 10.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1129 | Ashik Kasim | 2023-08-14 08:50 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1130 | 8fbfab4e080104e0 |  | Margham | Area 25 | MEC-Compressor B | 24.9749387,55.6182752 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZT-221 | 25-ZT-221 | POSITION TRANSMITTER, TEMPERATURE CONTROL VALVE COOLING GAS | FISHER | DVC6200 | F002085251 | Instrumentation | Not available | Gb | IEC | Ex d ia | IIC | T5 | IP66/68 | -40 +80 | CSA | IECExCSA16.0003X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1130 | Ashik Kasim | 2023-08-14 09:02 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1131 | 84c1ab4e080104e0 |  | Margham | Area 25 | MEC-Compressor B | 24.9749108,55.6179103 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZT-222 | 25-ZT-222 | POSITION TRANSMITTER, TEMPERATURE CONTROL VALVE COOLING GAS | Fisher | DVC6200 | F002086254 | Instrumentation | Not available | Ga | IEC | Ex d ia | IIC | T5 | IP66/68 | -40 +80 | CSA | IECExCSA16.0003X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1131 | Ashik Kasim | 2023-08-14 09:14 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1132 | ebc1ab4e080104e0 |  | Margham | Area 25 | MEC-Compressor B | 24.9749642,55.6179774 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZT-223 | 25-ZT-223 | POSITION TRANSMITTER, TEMPERATURE CONTROL VALVE COOLING GAS | Fisher | DVC6200 | F002086252 | Instrumentation | Not available | Ga | IEC | Ex d ia | IIC | T5 | IP66/68 | -40 +80 | CSA | IECExCSA16.0003X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1132 | Ashik Kasim | 2023-08-14 09:18 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1133 | 2bc2ab4e080104e0 |  | Margham | Area 25 | MEC-Compressor B | 24.9748017,55.6181074 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-GT-223A | 25-GT-223A | GAS DETECTOR TRANSMITTER | MSA | UltimaX5000 | 000100000126007D | Instrumentation | 2 | Gb | IEC | Ex d | IIC | T5 | Not available | -40 +60 | SIRA | IECEX SIR17.0017X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1133 | Ashik Kasim | 2023-08-14 09:27 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1134 | aebfab4e080104e0 |  | Margham | Area 25 | MEC-Compressor B | 24.9750124,55.6180096 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-GT-223B | 25-GT-223B | GAS DETECTOR TRANSMITTER | MSA | UltimaX5000 | 00010000012701D6 | Instrumentation | 2 | Gb | IEC | Ex d | IIC | T5 | Not available | -40 +60 | SIRA | IECEX SIR17.0017X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1134 | Ashik Kasim | 2023-08-14 09:45 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1135 | c1c2ab4e080104e0 |  | Margham | Area 25 | MEC-Compressor B | 24.974967,55.618021 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-GT-222B | 25-GT-222B | GAS DETECTOR TRANSMITTER | MSA | UltimaX5000 | 000100000128000B | Instrumentation | 2 | Gb | IEC | Ex d | IIC | T5 | Not available | -40 +60 | SIRA | IECEX SIR17.0017X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1135 | Ashik Kasim | 2023-08-14 09:48 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1136 | a5bfab4e080104e0 |  | Margham | Area 25 | MEC-Compressor B | 24.9750075,55.6180372 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-GT-222A | 25-GT-222A | GAS DETECTOR TRANSMITTER | MSA | UltimaX5000 | 0001000001280055 | Instrumentation | 2 | Gb | IEC | Ex d | IIC | T5 | Not available | -40 +60 | SIRA | IECEX SIR17.0017X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1136 | Ashik Kasim | 2023-08-14 09:52 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1137 | 9ebeab4e080104e0 |  | Margham | Area 25 | MEC-Compressor B | 24.9749445,55.6179852 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PDIT-224 | 25-PDIT-224 | DP TRANSMITTER, COOLING GAS | Rosemount | 3051CD3A02A1BWR3S5E7M5Q4Q8QTD4 | 0500213 | Instrumentation | Not available | Ga | IEC | Ex db | IIC | T5 | IP66/68 | -20 +85 | BAS | IECEx BAS 10.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1137 | Ashik Kasim | 2023-08-14 09:59 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1138 | e15dab4e080104e0 |  | Margham | Area 25 | MEC-Compressor B | 24.9749874,55.6179218 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-224 | 25-TIT-224 | TEMPERATURE TRANSMITTER, COOLING GAS SYSTEM COMPRESSOR-B | Rosemount | 3144P | 5123892 | Instrumentation | Not available | Gb | IEC | Ex db | IIC | T5 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1138 | Ashik Kasim | 2023-08-14 10:07 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1139 | 8cc1ab4e080104e0 |  | Margham | Area 25 | MEC-Compressor B | 24.9749579,55.6179286 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-226 | 25-TIT-227 | TEMPERATURE TRANSMITTER, COOLING GAS SYSTEM COMPRESSOR-B | Rosemount | 3144P | 5123893 | Instrumentation | Not available | Gb | IEC | Ex db | IIC | T5 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1139 | Ashik Kasim | 2023-08-14 10:12 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1140 | cfc1ab4e080104e0 |  | Margham | Area 25 | MEC-Compressor B | 24.9749509,55.617933 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-227 | 25-TIT-227 | TEMPERATURE TRANSMITTER, COOLING GAS SYSTEM COMPRESSOR-B | Rosemount | 3144P | 512384 | Instrumentation | Not available | Gb | IEC | Ex db | IIC | T5 | IP66 | -50 +60 | FMG | IECExFMG12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1140 | Ashik Kasim | 2023-08-14 10:17 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1141 | 49beab4e080104e0 |  | Margham | Area 25 | MEC-Compressor B | 24.9749893,55.6179707 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TE-224 | 25-TE-224 | RTD, COOLING GAS SYSTEM COMPRESSOR-B | Rosemount | 0065CN1N0000N0245E7TB | 5064332 | Instrumentation | Not available | Gb | IEC | Ex db | IIC | T5 | Not available | -50 +80 | FMG | IECExFMG12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1141 | Ashik Kasim | 2023-08-14 10:27 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1142 | d3c0ab4e080104e0 |  | Margham | Area 25 | MEC-Compressor B | 24.9749677,55.6179291 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-JB-224 | CA_25-JB-224-01 | Ex e Junction Box | General Electric | E2B 800-1000-300 | 18A008-002 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T4 | Not available | -30 +60 | INE | IECExINE19.0019X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1142 | Ashik Kasim | 2023-08-14 10:32 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1143 | a8c5ab4e080104e0 |  | Margham | Area 25 | MEC-Compressor B | 24.9749238,55.6179013 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-EJB-223 | CA_25-EJB-223 | Ex e Junction Box | General Electric | E2B 800-1000-300 | 18A008-002 | Electrical | 2 | Gb | IEC | Ex eb | IIC | T4 | Not available | -30 +60 | INE | IECExINE19.0019X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1143 | Ashik Kasim | 2023-08-14 10:40 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1144 | 2CC1AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor B | 55.6179646,24.9749833 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-EJB-221 | 25-MPC-18A | Ex d - Junction Box | General Electric | E2B 760-1100-300 | 18A008-002 | Electrical | 2 | Gb | IEC | Ex d | IIC | T4 | Not Available | -30 +60 | INE | IECExINE190019X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1144 | Ashik Kasim | 2023-08-15 15:25 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1145 | 3FC2AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor B | 55.6179662,24.9750249 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IJB-221 | CD_25-IJB-221 | Junction Box IS | Technor | Not available | 19/00194 | Instrumentation | Not Available | Gb | IEC | Ex ia | IIC | T6 | IP66 | 0 +60 | IMQ | IECExIMQ15.0002X | Yes | Others | Periodic | i | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1145 | Ashik Kasim | 2023-08-15 15:30 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1146 | ACBFAB4E080104E0 |  | Margham | Area 25 | MEC-Compressor B | 55.6179851,24.9749968 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-JB-226 | CA _25-JB-226 | Junction Box | STAHIL | 8150/1-0600-600-150-3321 | Not available | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T4 | IP66 | -50 +60 | PTB | IECExPTB09.0048 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1146 | Ashik Kasim | 2023-08-15 15:33 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1147 | 5AC1AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor B | 55.6179985,24.9750713 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-JB-225 | CA _25-JB-225 | Junction Box | STAHIL | 8150/1-0400-400-150-3321 | Not available | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T4 | IP66 | -50 +60 | PTB | IECExPTB09.0048 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1147 | Ashik Kasim | 2023-08-15 15:35 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1148 | 49C0AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor B | 55.6180541,24.9749944 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PBESD-221 | CD_25-PBESD-221 | ESD 3 MEC-1 SHUTDOWN MEC-1 SKID | STAHIL | 8150/5-0176-0116-091-3311 | Not available | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T4 | IP66 | -60 +60 | PTB | IECExPTB09.0049 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1148 | Ashik Kasim | 2023-08-15 15:41 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1149 | B2C0AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor B | 55.6180016,24.975074 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-EJB-222 | 25-MPC-16A | Ex e - Junction Box | General Electric | E2B 1200x970x600 | 18A008-002 | Electrical | 2 | Gb | IEC | Ex eb | IIC | T4 | Not Available | -30 +60 | INE | IECExINE190019X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1149 | Ashik Kasim | 2023-08-15 16:10 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1150 | C1BEAB4E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6179765,24.9747159 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2531 | CA_25-AE-2531 | FLAMMABLE GAS DETECTOR - IR POINT TYPE | Net Safety | SC311S-100-ASSY | 085911 | Instrumentation | Not Available | Gb | IEC | Ex d | IIB + H2 | T5 | IP64 | -40 +75 | FMG | IECExFMG 12.0007X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1150 | Ashik Kasim | 2023-08-16 05:42 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1151 | 51BEAB4E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6179641,24.974733 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-324 | 25-PIT-324 | PRESSURE TRANSMITTER, COOLING GAS SYSTEM COMPRESSOR-C | Rosemount | Not visible | 0500060 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1151 | Ashik Kasim | 2023-08-16 05:44 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1152 | D0C0AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6179513,24.9746317 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-325 | 25-PIT-325 | PRESSURE TRANSMITTER, COOLING GAS SYSTEM COMPRESSOR-C | Rosemount | Not visible | 0500198 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1152 | Ashik Kasim | 2023-08-16 05:47 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1153 | F9BFAB4E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6179417,24.9746296 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TE-326 | 25-TE-326 | RTD, COOLING GAS SYSTEM COMPRESSOR-C | Rosemount | 0065CN1N0000N0245E7TB | 05064441 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T5 | Not Available | -50 +80 | FMG | IECExFMG12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1153 | Ashik Kasim | 2023-08-16 05:50 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1154 | 98C2AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6179673,24.9746081 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TE-327 | 25-TE-327 | RTD, COOLING GAS SYSTEM COMPRESSOR-C | Rosemount | 0065CN1N0000N0245E7TB | 05064442 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T5 | Not Available | -50 +80 | FMG | IECExFMG12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1154 | Ashik Kasim | 2023-08-16 05:53 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1155 | 325BAB4E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6179713,24.9745933 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-326 | 25-PIT-326 | PRESSURE TRANSMITTER, COOLING GAS SYSTEM COMPRESSOR-C | Rosemount | Not visible | 0500199 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1155 | Ashik Kasim | 2023-08-16 05:55 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1156 | C4C3AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6180575,24.9745619 | Zone 2 | IIC | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2532 | CA_25-AE-2532 | FLAMMABLE GAS DETECTOR - IR POINT TYPE | Net Safety | SC311S-100-ASSY | 085912 | Instrumentation | Not Available | Gb | IEC | Ex d | IIB + H2 | T5 | IP64 | -40 +75 | FMG | IECExFMG 12.0007X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1156 | Ashik Kasim | 2023-08-16 06:01 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1157 | 4EBEAB4E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6179236,24.9747088 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-331 | 25-PIT-331 | PRESSURE TRANSMITTER, COOLING GAS SYSTEM COMPRESSOR-C | Rosemount | Not visible | 0500063 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1157 | Ashik Kasim | 2023-08-16 06:05 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1158 | 5ABEAB4E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6179665,24.9747263 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-325 | CA_25-TIT-325 | TEMPERATURE TRANSMITTER, COOLING GAS SYSTEM COMPRESSOR-C | Rosemount | D1A2E7B4M5CNC4Q4U1QTXAK1105 | 5123900 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1158 | Ashik Kasim | 2023-08-16 06:07 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1159 | 79C1AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6180141,24.9747221 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-327 | 25-PIT-327 | PRESSURE TRANSMITTER, COOLING GAS SYSTEM COMPRESSOR-C | Rosemount | Not visible | 20WEPG0855649 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1159 | Ashik Kasim | 2023-08-16 06:10 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1160 | FABFAB4E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6180173,24.9746504 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PIT-328 | 25-PIT-328 | PRESSURE TRANSMITTER, COOLING GAS SYSTEM COMPRESSOR-C | Rosemount | Not visible | 0500205 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T6 | IP66/68 | -60 +70 | KEM | IECEx KEM 08.0010X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1160 | Ashik Kasim | 2023-08-16 06:14 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1161 | 5EC3AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6180593,24.9746599 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PDIT-323 | CA_25-PDIT-323 | DP TRANSMITTER, COOLING GAS | Rosemount | 3051CD3A02A1BWR3SE7M5Q4Q8QTD4 | 0500214 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T5 | IP66/68 | -20 +85 | BAD | IECEx BAS 10.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1161 | Ashik Kasim | 2023-08-16 06:17 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1162 | 46C0AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6180251,24.9747119 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZT-323 | 25-ZT-323 | POSITION TRANSMITTER, TEMPERATURE CONTROL VALVE COOLING GAS | FISHER | DVC6200 | F002086258 | Instrumentation | Not Available | Ga | IEC | Ex d ia | IIC | T5 | IP66/68 | -40 +80 | CSA | IECExCSA16.0003X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1162 | Ashik Kasim | 2023-08-16 06:20 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1163 | E030AA4E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.617954,24.9748723 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZT-322 | 25-ZT-322 | POSITION TRANSMITTER, TEMPERATURE CONTROL VALVE COOLING GAS | FISHER | DVC6200 | F002086255 | Instrumentation | Not Available | Ga | IEC | Ex d ia | IIC | T5 | IP66/68 | -40 +80 | CSA | IECExCSA16.0003X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1163 | Ashik Kasim | 2023-08-16 06:26 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1164 | 26C2AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6180441,24.9746649 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-ZT-321 | 25-ZT-321 | POSITION TRANSMITTER, TEMPERATURE CONTROL VALVE COOLING GAS | FISHER | DVC6200 | F002086250 | Instrumentation | Not Available | Ga | IEC | Ex d ia | IIC | T5 | IP66/68 | -40 +80 | CSA | IECExCSA16.0003X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1164 | Ashik Kasim | 2023-08-16 06:34 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1165 | E2C0AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6181009,24.974617 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-GT-323A | 25-GT-323A | GAS DETECTOR TRANSMITTER | MSA | UltimaX5000 | 00010000012800C3 | Instrumentation | 2 | Gb | IEC | Ex d | IIC | T5 | Not Available | -40 +60 | SIRA | IECEX SIR17.0017X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1165 | Ashik Kasim | 2023-08-17 05:44 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1166 | A7BEAB4E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6180828,24.9746464 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-GT-323B | 25-GT-323B | GAS DETECTOR TRANSMITTER | MSA | UltimaX5000 | 0001000001280019 | Instrumentation | 2 | Gb | IEC | Ex d | IIC | T5 | Not Available | -40 +60 | SIRA | IECEX SIR17.0017X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1166 | Ashik Kasim | 2023-08-17 05:47 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1167 | 9BC1AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6180759,24.9747163 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-GT-322B | 25-GT-322B | GAS DETECTOR TRANSMITTER | MSA | UltimaX5000 | 0001000001280032 | Instrumentation | 2 | Gb | IEC | Ex d | IIC | T5 | Not Available | -40 +60 | SIRA | IECEX SIR17.0017X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1167 | Ashik Kasim | 2023-08-17 05:50 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1168 | 83C4AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6180473,24.9747357 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-GT-322A | 25-GT-322A | GAS DETECTOR TRANSMITTER | MSA | UltimaX5000 | 0001000001280033 | Instrumentation | 2 | Gb | IEC | Ex d | IIC | T5 | Not Available | -40 +60 | SIRA | IECEX SIR17.0017X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1168 | Ashik Kasim | 2023-08-17 05:54 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1169 | F9C2AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.618051,24.9746867 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-EJB-321 | 25-MPC-17A | Ex d - Junction Box | General Electric | E2B 760-1100-300 | 18A008-003 | Electrical | 2 | Gb | IEC | Ex d | IIC | T4 | Not Available | -30 +60 | INE | IECExINE190019X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1169 | Ashik Kasim | 2023-08-17 05:59 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1170 | F1C4AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.618091,24.9747237 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-IJB-321 | CD_25-IJB-321 | Junction Box IS | Technor | Not available | 19/00182 | Instrumentation | Not Available | Gb | IEC | Ex ia | IIC | T6 | IP66 | 0 +60 | IMQ | IECExIMQ15.0002X | Yes | Others | Periodic | i | Close | A6. Circuit id not available | A6. Fix circuit id |  | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 1170 | Ashik Kasim | 2023-08-17 06:03 | A6. Pending | 1 |  | Yellow | 5 | Minor Repair Required | Not Applicable | Not Applicable
1171 | CEC1AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6180591,24.9747251 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-JB-326 | CA _25-JB-326 | Junction Box | STAHIL | 8150/1-0600-600-150-3321 | Not available | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T4 | IP66 | -50 +60 | PTB | IECExPTB09.0048 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1171 | Ashik Kasim | 2023-08-17 06:08 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1172 | C5C2AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6180125,24.9746282 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-JB-325 | CA _25-JB-325 | Junction Box | STAHIL | 8150/1-0400-400-150-3321 | Not available | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T4 | IP66 | -50 +60 | PTB | IECExPTB09.0048 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1172 | Ashik Kasim | 2023-08-17 06:10 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1173 | 20C0AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.618039,24.9746203 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PBESD-321 | CD_25-PBESD-321 | ESD 3 MEC-3 SHUTDOWN MEC-1 SKID | STAHIL | 8150/5-0176-0116-091-3311 | Not available | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T4 | IP66 | -60 +60 | PTB | IECExPTB09.0049 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1173 | Ashik Kasim | 2023-08-17 06:12 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1174 | 07C6AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6179783,24.9746603 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-EJB-322 | 25-MPC-005A | Ex e - Junction Box | General Electric | E2B 1200x970x600 | 18A008-003 | Electrical | 2 | Gb | IEC | Ex eb | IIC | T4 | Not Available | -30 +60 | INE | IECExINE190019X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1174 | Ashik Kasim | 2023-08-17 06:18 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1175 | 63C1AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6179055,24.9747337 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-324 | 25-TIT-324 | TEMPERATURE TRANSMITTER, COOLING GAS SYSTEM COMPRESSOR-A | Rosemount | 3144P | 5123895 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1175 | Ashik Kasim | 2023-08-17 06:22 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1176 | 07C2AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6179354,24.9747279 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-PDIT-324 | CA_25-PDIT-324 | DP TRANSMITTER, COOLING GAS | Rosemount | 3051CD3A02A1BWR3SE7M5Q4Q8QTD4 | 0500215 | Instrumentation | Not Available | Ga | IEC | Ex db | IIC | T5 | IP66/68 | -20 +85 | BAD | IECEx BAS 10.0034X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1176 | Ashik Kasim | 2023-08-17 06:24 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1177 | BCC0AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6179148,24.9746958 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-JB-324 | CA_25-JB-324-01 | Ex e - Junction Box | General Electric | E2B 800-1000-300 | 18A008-003 | Electrical | 2 | Gb | IEC | Ex eb | IIC | T4 | Not Available | -30 +60 | INE | IECExINE190019X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1177 | Ashik Kasim | 2023-08-17 06:29 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1178 | 5DC0AB4E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6190707,24.9781934 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-EJB-323 | 25-PC-751 | Ex e - Junction Box | General Electric | E2B 800-1000-300 | 18A008-003 | Electrical | 2 | Gb | IEC | Ex eb | IIC | T4 | Not Available | -30 +60 | INE | IECExINE190019X | Yes | Others | Periodic | e | Close | A4. Inappropriate IP protection | A4. Install IP washer | IP Washer Not Available | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Normal |  | Data Sheet 1178 | Ashik Kasim | 2023-08-17 11:27 | A4. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Normal | Ashik Kasim | 2023-09-08 16:45
1179 | 612BB64C080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6178657,24.9748065 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-326 | 25-TIT-326 | TEMPERATURE TRANSMITTER, COOLING GAS SYSTEM COMPRESSOR-C | Rosemount | 3144P | 5123896 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1179 | Ashik Kasim | 2023-08-21 05:47 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1180 | 4892A64E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6179223,24.974727 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TIT-327 | 25-TIT-327 | TEMPERATURE TRANSMITTER, COOLING GAS SYSTEM COMPRESSOR-C | Rosemount | 3144P | 5123897 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T6 | IP66 | -50 +60 | FMG | IECEx FMG 12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1180 | Ashik Kasim | 2023-08-21 05:50 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1181 | C990A64E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6179328,24.9746841 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-TE-324 | 25-TE-324 | RTD, COOLING GAS SYSTEM COMPRESSOR-C | Rosemount | 0065CN1N0000N0245E7TB | 05064333 | Instrumentation | Not Available | Gb | IEC | Ex db | IIC | T5 | Not Available | -50 +80 | FMG | IECExFMG12.0022X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1181 | Ashik Kasim | 2023-08-21 05:54 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1182 | 6D90A64E080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6178572,24.9747267 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2561 | CA_25-AE-2561 | TRIPLE IR FLAME DETECTOR | Rosemount | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T4 | IP68 | -60 +85 | Sira | Sira15ATEX1364X | Yes | Others | Periodic | d | Close | A10. Wrong type blanking elements installed | A10. Replace with suitable type blanking elements | Teflon tape used | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1182 | Ashik Kasim | 2023-08-21 06:24 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-08-28 09:42
1183 | DE2BB64C080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6179176,24.9746113 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2562 | CA_25-AE-2562 | TRIPLE IR FLAME DETECTOR | Rosemount | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T4 | IP68 | -60 +85 | Sira | Sira15ATEX1364X | Yes | Others | Periodic | d | Close | A10. Wrong type blanking elements installed | A10. Replace with suitable type blanking elements | Teflon tape used | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1183 | Ashik Kasim | 2023-08-21 06:26 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-08-28 09:37
1184 | 232CB64C080104E0 |  | Margham | Area 25 | MEC-Compressor C | 55.6178421,24.9745592 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HS-2536 | CD_25-HS-2536 | MANUAL CALL POINT | EATON | SM87PBLD | 2156858197113 | Instrumentation | Not Available | Gb | IEC | Ex d | IIC | T5 | IP66/67 | -55 +70 | BAS | IECEx BAS 09.0060 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1184 | Ashik Kasim | 2023-08-21 06:29 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1185 | 758FA64E080104E0 |  | Margham | Area 25 | MEC-Compressor B | 55.6178806,24.9748285 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HS-2526 | CD_25-HS-2526 | MANUAL CALL POINT | EATON | SM87PBLD | 2156858197109 | Instrumentation | Not Available | Gb | IEC | Ex d | IIC | T5 | IP66/67 | -55 +70 | BAS | IECEx BAS 09.0060 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1185 | Ashik Kasim | 2023-08-21 06:32 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1186 | A52CB64C080104E0 |  | Margham | Area 25 | MEC-Compressor B | 55.6179936,24.9748862 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2552 | CA_25-AE-2552 | TRIPLE IR FLAME DETECTOR | Rosemount | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T4 | IP68 | -60 +85 | Sira | Sira15ATEX1364X | Yes | Others | Periodic | d | Close | A10. Wrong type blanking elements installed | A10. Replace with suitable type blanking elements | Teflon tape used | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1186 | Ashik Kasim | 2023-08-21 06:34 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-08-28 09:47
1187 | 9A91A64E080104E0 |  | Margham | Area 25 | MEC-Compressor B | 55.6179428,24.9749341 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2551 | CA_25-AE-2551 | TRIPLE IR FLAME DETECTOR | Rosemount | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T4 | IP68 | -60 +85 | Sira | Sira15ATEX1364X | Yes | Others | Periodic | d | Close | A10. Wrong type blanking elements installed | A10. Replace with suitable type blanking elements | Teflon tape used | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1187 | Ashik Kasim | 2023-08-21 06:36 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-08-28 09:52
1188 | 3C8FA64E080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.6179697,24.9751844 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2542 | CA_25-AE-2542 | TRIPLE IR FLAME DETECTOR | Rosemount | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T4 | IP68 | -60 +85 | Sira | Sira15ATEX1364X | Yes | Others | Periodic | d | Close | A10. Wrong type blanking elements installed | A10. Replace with suitable type blanking elements | Teflon tape used | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1188 | Ashik Kasim | 2023-08-21 06:41 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-08-28 10:07
1189 | 3029B64C080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.6177618,24.9752791 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2541 | CA_25-AE-2541 | TRIPLE IR FLAME DETECTOR | Rosemount | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T4 | IP68 | -60 +85 | Sira | Sira15ATEX1364X | Yes | Others | Periodic | d | Close | A10. Wrong type blanking elements installed | A10. Replace with suitable type blanking elements | Teflon tape used | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1189 | Ashik Kasim | 2023-08-21 06:46 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-08-28 09:55
1190 | 5093A64E080104E0 |  | Margham | Area 25 | Substation Building (South Side) Near HVAC Unit | 55.6176822,24.9742747 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XA-2501G | CD_25-XA-2501G | SINGLE TONE SOUNDER (WITH ADJUSTABLE TONE & VOLUME)-GAS | EATON | DB3BG | 2156858196104 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T4 | Not Available | -55 +85 | Baseefa | Baseefa13ATEX0229X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1190 | Ashik Kasim | 2023-08-21 08:58 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1191 | BE90A64E080104E0 |  | Margham | Area 25 | Substation Building (South Side) Near HVAC Unit | 55.6176712,24.9742763 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XA-2501F | CD_25-XA-2501F | SINGLE TONE SOUNDER (WITH ADJUSTABLE TONE & VOLUME)-FIRE | EATON | DB3BG | 2156858196101 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T4 | Not Available | -55 +85 | Baseefa | Baseefa13ATEX0229X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1191 | Ashik Kasim | 2023-08-21 09:01 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1192 | 3990A64E080104E0 |  | Margham | Area 25 | Substation Building (South Side) Near HVAC Unit | 55.6176725,24.9742757 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XL-2501G | CD_25-XL-2501G | FLASHING BEACON (WITH RED GLASS FOR FIRE & BLUE GLASS FOR GAS) | EATON | XB4 | 2156958195101 | Instrumentation | Not Available | Gb | IEC | Ex d | IIC | T4 | IP65 | -55 +60 | BAS | IECExBAS10.0078X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1192 | Ashik Kasim | 2023-08-21 09:05 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1193 | 552CB64C080104E0 |  | Margham | Area 25 | Substation Building (South Side) Near HVAC Unit | 55.6176586,24.9742989 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-XL-2501F | CD_25-XL-2501F | FLASHING BEACON (WITH RED GLASS FOR FIRE & BLUE GLASS FOR GAS) | EATON | XB4 | 2156958194101 | Instrumentation | Not Available | Gb | IEC | Ex d | IIC | T4 | IP65 | -55 +60 | BAS | IECExBAS10.0078X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1193 | Ashik Kasim | 2023-08-21 09:12 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1194 | 5429B64C080104E0 |  | Margham | Area 25 | Substation Building (South Side) Near HVAC Unit | 55.6176972,24.9742843 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HS-2526 | CD_25-HS-2526 | MANUAL CALL POINT | EATON | SM87PBLD | 2156858197102 | Instrumentation | Not Available | Gb | IEC | Ex d | IIC | T5 | IP66/67 | -55 +70 | BAS | IECEx BAS 09.0060 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1194 | Ashik Kasim | 2023-08-21 09:16 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1195 | 7329B64C080104E0 |  | Margham | Area 25 | Substation Building (South Side) Near HVAC Unit | 55.617697,24.9742305 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-FJBD-2501 | CD_25-FJBD-2501 | INSTRUMENT JUNCTION BOX | Weidmuller | KLIPPON TB MH453820S4N1 | XB-AE-A-039397 | Instrumentation | 2 | Gb | IEC | Ex eb | IIC | T6 | IP66 | -20 +55 | IBE | IBExU14ATEX1050 | Not applicable | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1195 | Ashik Kasim | 2023-08-21 09:22 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1196 | FA29B64C080104E0 |  | Margham | Area 25 | MEC 03 Compressor Skid-Top | 55.6179753,24.9747082 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-182 | 25-PC-598 | LIGHTING JUNCTION BOX | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040148 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECExIBE13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1196 | Ashik Kasim | 2023-08-21 09:46 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1197 | 3F29B64C080104E0 |  | Margham | Area 25 | MEC 03 Compressor Skid-Top | 55.6179847,24.9746233 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HBL-302 | 25-PC-598 | LED HIGH BAY LIGHTING, 25-MCB-DB-002F13 | EATON | NFMVA25LCY/UNV1 76 | Not Available | Electrical | 3 | Gc | IEC | Ex ec | IIC | T4 | Not Available | -40 +55 | DEMKO | DEMKO15ATEX1377X | Yes | Lighting | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Scaffolding |  | Data Sheet 1197 | Ashik Kasim | 2023-08-21 09:58 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Scaffolding
1198 | 3D2DB64C080104E0 |  | Margham | Area 25 | MEC 03 Compressor Skid-Top | 55.61794,24.9745267 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-193 | 25-PC-621 | LIGHTING JUNCTION BOX | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040180 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECExIBE13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1198 | Ashik Kasim | 2023-08-21 10:02 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1199 | 3B91A64E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Skid-Top | 55.6179669,24.974485 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HBL-305 | 25-PC-620 | LED HIGH BAY LIGHTING, 25-MCB-DB-002F14 | EATON | NFMVA25LCY/UNV1 76 | Not Available | Electrical | 3 | Gc | IEC | Ex ec | IIC | T4 | Not Available | -40 +55 | DEMKO | DEMKO15ATEX1377X | Yes | Lighting | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Scaffolding |  | Data Sheet 1199 | Ashik Kasim | 2023-08-21 10:06 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Scaffolding
1200 | F691A64E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Skid-Top | 55.6181488,24.9745641 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-192 | 25-PC-623 | LIGHTING JUNCTION BOX | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040400 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECExIBE13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1200 | Ashik Kasim | 2023-08-21 10:14 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1201 | CC91A64E080104E0 |  | Margham | Area 25 | MEC 03 Compressor Skid-Top | 55.6179669,24.974485 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HBL-304 | 25-PC-620 | LED HIGH BAY LIGHTING, 25-MCB-DB-002F14 | EATON | NFMVA25LCY/UNV1 76 | Not Available | Electrical | 3 | Gc | IEC | Ex ec | IIC | T4 | Not Available | -40 +55 | DEMKO | DEMKO15ATEX1377X | Yes | Lighting | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Scaffolding |  | Data Sheet 1201 | Ashik Kasim | 2023-08-21 10:19 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Scaffolding
1202 | 192CB64C080104E0 |  | Margham | Area 25 | MEC 03 Compressor Skid-Top | 55.6179561,24.9746402 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-183 | 25-PC-599 | LIGHTING JUNCTION BOX | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040089 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECExIBE13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1202 | Ashik Kasim | 2023-08-21 10:30 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1203 | B82CB64C080104E0 |  | Margham | Area 25 | MEC 03 Compressor Skid-Top | 55.6180404,24.9746693 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HBL-301 | 25-PC-600 | LED HIGH BAY LIGHTING, 25-MCB-DB-002F13 | EATON | NFMVA25LCY/UNV1 76 | Not Available | Electrical | 3 | Gc | IEC | Ex ec | IIC | T4 | Not Available | -40 +55 | DEMKO | DEMKO15ATEX1377X | Yes | Lighting | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Scaffolding |  | Data Sheet 1203 | Ashik Kasim | 2023-08-21 10:35 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Scaffolding
1204 | A02AB64C080104E0 |  | Margham | Area 25 | Area 25 Substation North-Outdoor | 55.6170959,24.9752941 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HS-2540 | CD_25-HS-2540 | MANUAL CALL POINT | EATON | SM87PBLD | 2156858197101 | Instrumentation | Not Available | Gb | IEC | Ex d | IIC | T5 | IP66/67 | -55 +70 | BAS | IECEx BAS 09.0060 | Not applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1204 | Ashik Kasim | 2023-08-21 10:50 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1205 | 2C2DB64C080104E0 |  | Margham | Area 25 | Area 25 Substation North-Outdoor | 55.6170255,24.9750745 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-WLF-023 | 25-PC-723-B | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-102 | Electrical | Not Available | Gc | IEC | Ex db | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP18.0003X | Yes | Lighting | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Machineries |  | Data Sheet 1205 | Ashik Kasim | 2023-08-24 09:32 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Machineries
1206 | 5F29B64C080104E0 |  | Margham | Area 25 | Area 25 Substation North-Outdoor | 55.6171606,24.9751412 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2588D | FA/25-MB-2506/25-AE-2588D | GAS DETECTOR METHANE (F&G) | CROWCON | XgardIQ | Not Available | Instrumentation | 2 | Gb | IEC | Ex db ia | IIC | T4 | Not Available | Not Available | Baseefa | Baseefa14ATEX0012X | Yes | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Machineries |  | Data Sheet 1206 | Ashik Kasim | 2023-08-24 09:59 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Machineries
1207 | DF2AB64C080104E0 |  | Margham | Area 25 | Area 25 Substation North-Outdoor | 55.6171277,24.9751566 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-AE-2588C | FA/25-MB-2506/25-AE-2588C | GAS DETECTOR METHANE (F&G) | CROWCON | XgardIQ | Not Available | Instrumentation | 2 | Gb | IEC | Ex db ia | IIC | T4 | Not Available | Not Available | Baseefa | Baseefa14ATEX0012X | Yes | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Machineries |  | Data Sheet 1207 | Ashik Kasim | 2023-08-24 10:18 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Machineries
1208 | 9D8FA64E080104E0 |  | Margham | Area 25 | Area 25 Substation North-Outdoor | 55.6172157,24.975166 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-WLF-022 | 25-PC-722 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-101 | Electrical | Not Available | Gc | IEC | Ex db | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP18.0003X | Yes | Lighting | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Machineries |  | Data Sheet 1208 | Ashik Kasim | 2023-08-24 10:47 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Machineries
1209 | BE2CB64C080104E0 |  | Margham | Area 25 | Area 25 Substation Front Side-Outdoor | 55.6172624,24.9750042 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-WLF-021 | 25-PC-720 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-026 | Electrical | Not Available | Gc | IEC | Ex db | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP18.0003X | Yes | Lighting | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Machineries |  | Data Sheet 1209 | Ashik Kasim | 2023-08-24 11:10 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Machineries
1210 | 612CB64C080104E0 |  | Margham | Area 25 | Area 25 Substation Front Side-Outdoor | 55.6172109,24.9749761 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-WLF-020 | 25-PC-718 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-042 | Electrical | Not Available | Gc | IEC | Ex db | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP18.0003X | Yes | Lighting | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Machineries |  | Data Sheet 1210 | Ashik Kasim | 2023-08-25 10:47 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Machineries
1211 | 2090A64E080104E0 |  | Margham | Area 25 | Area 25 Substation Front Side-Outdoor | 55.6171269,24.9748075 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-WLF-019 | 25-PC-716 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-103 | Electrical | Not Available | Gc | IEC | Ex db | IIC | T6 | IP66 | -40 +55 | NEP | IECEx NEP18.0003X | Yes | Lighting | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Machineries |  | Data Sheet 1211 | Ashik Kasim | 2023-08-25 11:33 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Machineries
1212 | A72CB64C080104E0 |  | Margham | Area 95 | Maintenance Area-95-E-101(Top +30) | 55.6177443,24.9764712 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 057 | 95L-JB315-FL057-57 | Flood Light | Appleton | S-51HPS | GAM771LXR12 | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | Not available | Not Available | +40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available A3. Ambient temperature not suitable | A6. Fix equipment id A6. Fix circuit id A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1212 | Ashik Kasim | 2023-08-29 06:07 | A6. Pending A6. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable
1213 | 9B90A64E080104E0 |  | Margham | Area 95 | Maintenance Area-95-E-101(Top +30) | 55.617659,24.9763312 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 056 | 95L-JB315-FL056-56 | Flood Light | Appleton | S-51HPS | GAM771LXR12 | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | Not available | Not Available | +40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available A3. Ambient temperature not suitable | A6. Fix equipment id A6. Fix circuit id A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1213 | Ashik Kasim | 2023-08-29 06:07 | A6. Pending A6. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable
1214 | 3F2CB64C080104E0 |  | Margham | Area 95 | Maintenance Area-95-E-101(Top +30) | 55.6177653,24.9763644 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 027 | 95L-JB316-ST027-027 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1214 | Ashik Kasim | 2023-08-29 06:42 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1215 | B8C4AB4E080104E0 |  | Margham | Area 95 | Maintenance Area-95-E-101(Stair Ways) | 55.6177778,24.9763749 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 022 | 95L-JB316-ST022-022 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1215 | Ashik Kasim | 2023-08-29 06:42 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1216 | 5293A64E080104E0 |  | Margham | Area 95 | Maintenance Area-95-E-101(Stair Ways) | 55.6178283,24.9763991 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 028 | 95L-JB316-ST028-028 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available A6. Circuit id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id A6. Fix circuit id |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1216 | Ashik Kasim | 2023-08-29 06:40 | A3. Pending A6. Pending A6. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1217 | 4D2BB64C080104E0 |  | Margham | Area 95 | Maintenance Area-95-E-101(+30 Top) | 55.6178197,24.9763314 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 021 | 95L-JB316-ST021-021 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1217 | Ashik Kasim | 2023-08-30 05:36 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1218 | 44ADAB4E080104E0 |  | Margham | Area 95 | Maintenance Area-95-E-101(+30 Top) | 55.6176758,24.9763178 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 026 | 95L-JB317-ST026-026 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1218 | Ashik Kasim | 2023-08-30 05:43 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1219 | 852CB64C080104E0 |  | Margham | Area 95 | Maintenance Area-95-E-101(+30 Top) | 55.6175538,24.9763358 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 020 | 95L-JB316-ST020-020 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1219 | Ashik Kasim | 2023-08-30 05:47 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1220 | 5190A64E080104E0 |  | Margham | Area 95 | Maintenance Area-95-E-101(+30 Top) | 55.6175995,24.9763693 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 025 | 95L-JB316-ST025-025 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1220 | Ashik Kasim | 2023-08-30 05:54 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1221 | 4C2CB64C080104E0 |  | Margham | Area 95 | Maintenance Area-95-E-101(+30 Top) | 55.6175963,24.9764802 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 024 | 95L-JB316-ST024-024 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1221 | Ashik Kasim | 2023-08-30 05:59 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1222 | 072CB64C080104E0 |  | Margham | Area 95 | Maintenance Area-95-E-101(+30 Top) | 55.6176421,24.9764852 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 029 | 95L-JB31#-ST029-029 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1222 | Ashik Kasim | 2023-08-30 06:03 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1223 | F42AB64C080104E0 |  | Margham | Area 95 | Maintenance Area-95-E-101(+30 Top) | 55.6176547,24.9764795 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 023 | 95L-JB316-ST023-023 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1223 | Ashik Kasim | 2023-08-30 06:08 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1224 | 578FA64E080104E0 |  | Margham | Area 95 | 95-E-101(Top +30)Near Scrubber Area | 55.6176226,24.9764959 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 058 | 95L-JB315-FL058-049 | Flood Light | Appleton | S-51HPS | GAM771LXR12 | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | Not available | Not Available | +40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1224 | Ashik Kasim | 2023-08-30 06:42 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable
1225 | 9829B64C080104E0 |  | Margham | Area 95 | 95-E-101(Top +30)Near Scrubber Area | 55.6175717,24.9765163 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 031 | 95L-JB320-ST031-031 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1225 | Ashik Kasim | 2023-08-30 06:41 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1226 | AE8FA64E080104E0 |  | Margham | Area 95 | 95-E-101(Top +30)Near Scrubber Area | 55.6175402,24.976591 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 034 | 95L-JB317-ST034--034 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1226 | Ashik Kasim | 2023-08-30 08:46 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1227 | A22BB64C080104E0 |  | Margham | Area 95 | 95-E-101(Top +30)Near Scrubber Area | 55.6174988,24.9765761 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 035 | 95L-JB320-ST035--035 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1227 | Ashik Kasim | 2023-08-30 08:52 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1228 | CD2CB64C080104E0 |  | Margham | Area 95 | 95-E-101(Top +30)Near Scrubber Area | 55.6174285,24.9765665 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 033 | 95L-JB319-ST033--033 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1228 | Ashik Kasim | 2023-08-30 09:04 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1229 | 2091A64E080104E0 |  | Margham | Area 95 | 95-E-101(Top +30)Near Scrubber Area | 55.6175507,24.97656 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 032 | 95L-JB320-ST032--032 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1229 | Ashik Kasim | 2023-08-30 09:12 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1230 | 842AB64C080104E0 |  | Margham | Area 95 | 95-E-101(Top +30)Near Scrubber Area | 55.617628,24.9765249 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 030 | 95L-JB320-ST030-030 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1230 | Ashik Kasim | 2023-08-30 09:20 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1231 | 9991A64E080104E0 |  | Margham | Area 95 | 95-E-101(Top +45)Near Scrubber Area | 55.6176203,24.9765711 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 043 | 95L-JB320-ST043-043 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1231 | Ashik Kasim | 2023-08-30 09:31 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1232 | 5390A64E080104E0 |  | Margham | Area 95 | 95-E-101(Top +45)Near Scrubber Area | 55.6175772,24.9766896 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 046 | 95L-JB-318-ST046-046 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1232 | Ashik Kasim | 2023-08-30 09:35 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1233 | AAF9A64E080104E0 |  | Margham | Area 95 | 95-E-101(Top +45)Near Scrubber Area | 55.6175486,24.9765677 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 044 | 95L-JB318-ST044-044 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1233 | Ashik Kasim | 2023-08-30 09:53 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1234 | D18FA64E080104E0 |  | Margham | Area 95 | 95-E-101(Top +45)Near Scrubber Area | 55.6175342,24.9766207 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 045 | 95L-JB320-ST045-045 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1234 | Ashik Kasim | 2023-08-30 10:00 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1235 | 2C90A64E080104E0 |  | Margham | Area 95 | 95-E-101(Top +25)Near Scrubber Area | 55.6177705,24.9766027 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 041 | 95L-JB320-ST041-41 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1235 | Ashik Kasim | 2023-08-30 10:22 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1236 | 5090A64E080104E0 |  | Margham | Area 95 | 95-E-101(Top +25)Near Scrubber Area | 55.6176159,24.9765597 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 042 | 95L-JB319-ST042-42 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1236 | Ashik Kasim | 2023-08-30 10:26 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1237 | 0CCDA64E080104E0 |  | Margham | Area 95 | 95-E-101(Top +25)Near Scrubber Area | 55.6176416,24.9766591 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 040 | 95L-JB319-ST040-40 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1237 | Ashik Kasim | 2023-08-30 10:34 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1238 | 568FA64E080104E0 |  | Margham | Area 95 | 95-E-101(Top +25)Near Scrubber Area | 55.6176172,24.9765672 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 039 | 95L-JB319-ST039-39 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1238 | Ashik Kasim | 2023-08-30 10:39 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1239 | B390A64E080104E0 |  | Margham | Area 95 | 95-E-101(Top +20)Near 95-HV-9703 | 55.6177685,24.9766964 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | Not Available | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available A6. Circuit id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id A6. Fix circuit id |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1239 | Ashik Kasim | 2023-08-30 10:51 | A3. Pending A6. Pending A6. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1240 | CC2AB64C080104E0 |  | Margham | Area 95 | 95-E-101(Top +20)Near 95-HV-9703 | 55.6177685,24.9766964 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | Not Available | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available A6. Circuit id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id A6. Fix circuit id |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1240 | Ashik Kasim | 2023-08-30 10:55 | A3. Pending A6. Pending A6. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1241 | 112BB64C080104E0 |  | Margham | Area 95 | 95-E-101(Top +20)Near 95-HV-9703 | 55.6176272,24.9766117 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | Not Available | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available A6. Circuit id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id A6. Fix circuit id |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1241 | Ashik Kasim | 2023-08-30 11:07 | A3. Pending A6. Pending A6. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1242 | DD8FA64E080104E0 |  | Margham | Area 95 | Discharge Gas Cooler-95-E-201(Top +30) | 55.6171528,24.9764647 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 123 | 95L-JB322-ST123-110 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1242 | Ashik Kasim | 2023-08-31 05:42 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1243 | 0292A64E080104E0 |  | Margham | Area 95 | Discharge Gas Cooler-95-E-201(Top +30) | 55.61715,24.9764777 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 129 | 95L-JB323-ST129-116 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1243 | Ashik Kasim | 2023-08-31 05:46 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1244 | 7E2AB64C080104E0 |  | Margham | Area 95 | Discharge Gas Cooler-95-E-201(Top +30) | 55.6170784,24.9764717 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 124 | 95L-JB322-ST124-111 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment unless proven otherwise |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1244 | Ashik Kasim | 2023-08-31 05:50 | A6. Pending A3. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1245 | 538FA64E080104E0 |  | Margham | Area 95 | Discharge Gas Cooler-95-E-201(Top +30) | 55.617092,24.9764302 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 125 | 95L-JB323-ST125-11 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment unless proven otherwise |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1245 | Ashik Kasim | 2023-08-31 05:54 | A6. Pending A3. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1246 | 302BB64C080104E0 |  | Margham | Area 95 | Discharge Gas Cooler-95-E-201(Top +30) | 55.6170617,24.9763516 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 120 | 95L-JB322-ST120-107 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment unless proven otherwise |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1246 | Ashik Kasim | 2023-08-31 06:02 | A6. Pending A3. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1247 | 818FA64E080104E0 |  | Margham | Area 95 | Discharge Gas Cooler-95-E-201(Top +30) | 55.6171435,24.9763002 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 126 | 95L-JB323-ST126-113 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment unless proven otherwise |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1247 | Ashik Kasim | 2023-08-31 06:07 | A6. Pending A3. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1248 | DE8FA64E080104E0 |  | Margham | Area 95 | Discharge Gas Cooler-95-E-201(Top +30) | 55.6171886,24.9763354 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 121 | 95L-JB322-ST121-108 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment unless proven otherwise |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1248 | Ashik Kasim | 2023-08-31 06:10 | A6. Pending A3. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1249 | AD29B64C080104E0 |  | Margham | Area 95 | Discharge Gas Cooler-95-E-201(Top +30) | 55.6171935,24.9763766 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 156 | Not Available | Flood Light | Appleton | S-51HPS | GAM771LXR12 | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | Not available | Not Available | +40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available A3. Ambient temperature not suitable | A6. Fix equipment id A6. Fix circuit id A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1249 | Ashik Kasim | 2023-08-31 06:16 | A6. Pending A6. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable
1250 | B891A64E080104E0 |  | Margham | Area 95 | Discharge Gas Cooler-95-E-201(Top +30) | 55.6171949,24.9764242 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 127 | 95L-JB323-ST127-114 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment unless proven otherwise |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1250 | Ashik Kasim | 2023-08-31 06:20 | A6. Pending A3. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1251 | B52CB64C080104E0 |  | Margham | Area 95 | Discharge Gas Cooler-95-E-201(Stair Ways) | 55.6172007,24.9764777 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 128 | 95L-JB323-ST127-115 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment unless proven otherwise |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1251 | Ashik Kasim | 2023-08-31 06:25 | A6. Pending A3. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1252 | 6A2BB64C080104E0 |  | Margham | Area 95 | Discharge Gas Cooler-95-E-201(Stair Ways) | 55.6173561,24.9764561 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 122 | 95L-JB322-ST122-109 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment unless proven otherwise |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1252 | Ashik Kasim | 2023-08-31 06:36 | A6. Pending A3. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1253 | 9B29B64C080104E0 |  | Margham | Area 95 | Scrubber Suction Area-95-E-101(+10) | 55.6173801,24.9765962 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 037 | 95L-JB320-ST037-037 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1253 | Ashik Kasim | 2023-08-31 08:23 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1254 | 8591A64E080104E0 |  | Margham | Area 95 | Scrubber Suction Area-95-E-101(+10) | 55.6174785,24.9766109 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 038 | 95L-JB318-ST038-038 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1254 | Ashik Kasim | 2023-08-31 08:30 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1255 | 9C90A64E080104E0 |  | Margham | Area 95 | Scrubber Suction Area-95-E-101(+10) | 55.6174188,24.9765197 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 036 | 95L-JB320-ST036-036 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1255 | Ashik Kasim | 2023-08-31 08:43 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1256 | 5B29B64C080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-101(+25 Deck) | 55.6176712,24.9762564 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 019 | 95L-JB317-ST19-19 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1256 | Ashik Kasim | 2023-08-31 09:13 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1257 | 912CB64C080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-101(+25 Deck) | 55.617655,24.976306 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 012 | 95L-JB316-ST012-012 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1257 | Ashik Kasim | 2023-08-31 09:21 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1258 | 9C2CB64C080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-101(+25 Deck) | 55.6175892,24.9764468 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 016 | 95L-JB317-ST016-016 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1258 | Ashik Kasim | 2023-08-31 09:35 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1259 | E390A64E080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-101(+25 Deck) | 55.6176788,24.9764127 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 014 | 95L-JB316-ST014-014 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1259 | Ashik Kasim | 2023-08-31 09:41 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1260 | BF90A64E080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-101(+25 Deck) | 55.6176678,24.9764069 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 013 | 95L-JB316-ST013-013 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1260 | Ashik Kasim | 2023-08-31 09:52 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1261 | 5F90A64E080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-101(+25 Deck) | 55.6177053,24.976449 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 018 | 95L-JB317-ST018-018 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1261 | Ashik Kasim | 2023-08-31 10:00 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1262 | D4BEAB4E080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-101(+25 Deck) | 55.6175646,24.9763139 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 017 | 95L-JB317-ST017-017 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1262 | Ashik Kasim | 2023-08-31 10:13 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1263 | EB29B64C080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-101(+25 Deck) | 55.6176109,24.9765212 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 015 | 95L-JB316-ST-015-015 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1263 | Ashik Kasim | 2023-08-31 10:31 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1264 | CD91A64E080104E0 |  | Margham | Area 95 | Pipe Rack (95-C-101) | 55.6176184,24.976255 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB306-PO61--052 | Pendant Light Fixture | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | IIC | T2 | IP66 | +40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1264 | Ashik Kasim | 2023-09-01 11:30 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1265 | 1D90A64E080104E0 |  | Margham | Area 95 | Pipe Rack (95-C-101) | 55.6176883,24.9761962 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB308-P065--056 | Pendant Light Fixture | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | IIC | T2 | IP66 | +40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1265 | Ashik Kasim | 2023-09-01 06:04 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1266 | 2F2DB64C080104E0 |  | Margham | Area 95 | Pipe Rack (95-C-101) | 55.6177558,24.976258 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB308-P066--057 | Pendant Light Fixture | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | IIC | T2 | IP66 | +40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1266 | Ashik Kasim | 2023-09-01 06:08 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1267 | DB1FB74C080104E0 |  | Margham | Area 95 | Pipe Rack (95-C-101) | 55.6176622,24.9761838 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB308-P062--053 | Pendant Light Fixture | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | IIC | T2 | IP66 | +40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1267 | Ashik Kasim | 2023-09-01 06:13 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1268 | 5492A64E080104E0 |  | Margham | Area 95 | Pipe Rack (95-C-101) | 55.6176413,24.976227 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB308-P067-058 | Pendant Light Fixture | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | IIC | T2 | IP66 | +40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1268 | Ashik Kasim | 2023-09-01 06:17 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1269 | 8429B64C080104E0 |  | Margham | Area 95 | Pipe Rack (95-C-101) | 55.6175809,24.9762167 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB306-P063-054 | Pendant Light Fixture | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | IIC | T2 | IP66 | +40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1269 | Ashik Kasim | 2023-09-01 06:23 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1270 | F791A64E080104E0 |  | Margham | Area 95 | Pipe Rack (95-C-101) | 55.6175809,24.9762167 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB308-P068-059 | Pendant Light Fixture | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | IIC | T2 | IP66 | +40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1270 | Ashik Kasim | 2023-09-01 06:31 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1271 | DB8FA64E080104E0 |  | Margham | Area 95 | Pipe Rack (95-C-101) | 55.617518,24.9764755 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB308-P069-060 | Pendant Light Fixture | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | IIC | T2 | IP66 | +40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1271 | Ashik Kasim | 2023-09-01 06:34 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1272 | C02CB64C080104E0 |  | Margham | Area 95 | Pipe Rack (95-C-101) | 55.617518,24.9764755 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB308-P064-055 | Pendant Light Fixture | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | IIC | T2 | IP66 | +40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable A10. Wrong type blanking elements installed | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise A10. Replace with suitable type blanking elements |  | 4 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1272 | Ashik Kasim | 2023-09-01 06:47 | A6. Pending A3. Pending A3. Pending A10. Pending | 4 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1273 | A629B64C080104E0 |  | Margham | Area 95 | Pipe Rack (95-C-101) | 55.6175794,24.97633 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB308-P070-061 | Pendant Light Fixture | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | IIC | T2 | IP66 | +40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1273 | Ashik Kasim | 2023-09-01 06:46 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1274 | 462BB64C080104E0 |  | Margham | Area 95 | Pipe Rack (95-C-201) | 55.6170014,24.9759633 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB309-P161-148 | Pendant Light Fixture | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | IIC | T2 | IP66 | +40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1274 | Ashik Kasim | 2023-09-01 08:44 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1275 | 1492A64E080104E0 |  | Margham | Area 95 | Pipe Rack (95-C-201) | 55.6170014,24.9759633 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB311-P165-152 | Pendant Light Fixture | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | IIC | T2 | IP66 | +40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1275 | Ashik Kasim | 2023-09-01 08:39 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1276 | D329B64C080104E0 |  | Margham | Area 95 | Pipe Rack (95-C-201) | 55.6171421,24.9762642 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB311-P166-153 | Pendant Light Fixture | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | IIC | T2 | IP66 | +40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1276 | Ashik Kasim | 2023-09-01 08:49 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1277 | 398CA64E080104E0 |  | Margham | Area 95 | Pipe Rack (95-C-201) | 55.6171172,24.9762215 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB309-P162-149 | Pendant Light Fixture | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | IIC | T2 | IP66 | +40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1277 | Ashik Kasim | 2023-09-01 08:55 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1278 | 322DB64C080104E0 |  | Margham | Area 95 | Pipe Rack (95-C-201) | 55.6168637,24.9763451 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB311-P167-154 | Pendant Light Fixture | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | IIC | T2 | IP66 | +40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1278 | Ashik Kasim | 2023-09-01 09:02 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1279 | 742CB64C080104E0 |  | Margham | Area 95 | Pipe Rack (95-C-201) | 55.6170095,24.9762758 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB309-P163-150 | Pendant Light Fixture | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | IIC | T2 | IP66 | +40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1279 | Ashik Kasim | 2023-09-01 09:09 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1280 | F92AB64C080104E0 |  | Margham | Area 95 | Pipe Rack (95-C-201) | 55.6170109,24.9763737 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB311-P168-155 | Pendant Light Fixture | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | IIC | T2 | IP66 | +40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1280 | Ashik Kasim | 2023-09-01 09:20 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1281 | 1A91A64E080104E0 |  | Margham | Area 95 | Pipe Rack (95-C-201) | 55.6169909,24.9766122 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB311-P169-156 | Pendant Light Fixture | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | IIC | T2 | IP66 | +40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1281 | Ashik Kasim | 2023-09-01 09:56 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1282 | 242BB64C080104E0 |  | Margham | Area 95 | Pipe Rack (95-C-201) | 55.6169543,24.9764781 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB309-P164-151 | Pendant Light Fixture | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | IIC | T2 | IP66 | +40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1282 | Ashik Kasim | 2023-09-01 10:02 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1283 | 882CB64C080104E0 |  | Margham | Area 95 | Pipe Rack (95-C-201) | 55.6169479,24.9765822 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB311-P169-156 | Pendant Light Fixture | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | IIC | T2 | IP66 | +40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1283 | Ashik Kasim | 2023-09-01 11:28 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1284 | 0E2BB64C080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-201(+25 Deck) | 55.6169998,24.9763595 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 112 | 95L-JB322-ST112-099 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1284 | Ashik Kasim | 2023-09-01 10:26 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1285 | D72AB64C080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-201(+25 Deck) | 55.6171506,24.9763253 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 119 | 95L-JB323-ST119-106 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1285 | Ashik Kasim | 2023-09-01 10:28 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1286 | EE90A64E080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-201(+25 Deck) | 55.6169767,24.9764591 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 116 | 95L-JB323-ST116-103 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1286 | Ashik Kasim | 2023-09-01 10:37 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1287 | BE8FA64E080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-201(+25 Deck) | 55.6171227,24.9764099 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 114 | 95L-JB322-ST114-101 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1287 | Ashik Kasim | 2023-09-01 10:39 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1288 | 8729B64C080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-201(+25 Deck) | 55.6171231,24.9764837 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 113 | 95L-JB322-ST113-100 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1288 | Ashik Kasim | 2023-09-01 10:46 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1289 | F28FA64E080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-201(+25 Deck) | 55.6172309,24.9764247 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 118 | 95L-JB323-ST118-105 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1289 | Ashik Kasim | 2023-09-01 10:54 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1290 | 782BB64C080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-201(+25 Deck) | 55.6171097,24.9764825 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 117 | 95L-JB323-ST117-104 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1290 | Ashik Kasim | 2023-09-01 11:19 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1291 | F129B64C080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-201(+25 Deck) | 55.6171569,24.9765079 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 115 | 95L-JB322-ST115-102 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1291 | Ashik Kasim | 2023-09-01 11:26 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1292 | 2F90A64E080104E0 |  | Margham | Area 95 | 95-E-201(Top +30)Near Scrubber Area | 55.6170547,24.9765278 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 130 | 95L-JB325-ST130-117 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1292 | Ashik Kasim | 2023-09-04 05:41 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1293 | 6520B74C080104E0 |  | Margham | Area 95 | 95-E-201(Top +30)Near Scrubber Area | 55.6171105,24.9765413 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 158 | 95L-JB327-FL158-145 | Flood Light | Appleton | S-51HPS | GAM771LXR12 | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | Not available | Not Available | +40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1293 | Ashik Kasim | 2023-09-04 05:44 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable
1294 | 5792A64E080104E0 |  | Margham | Area 95 | 95-E-201(Top +30)Near Scrubber Area | 55.6170911,24.9765421 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 131 | 95L-JB326-ST131-118 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1294 | Ashik Kasim | 2023-09-04 05:48 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1295 | 0B2BB64C080104E0 |  | Margham | Area 95 | 95-E-201(Top +30)Near Scrubber Area | 55.6170155,24.9765054 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 134 | 95L-JB323-ST134-121 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1295 | Ashik Kasim | 2023-09-04 05:54 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1296 | A991A64E080104E0 |  | Margham | Area 95 | 95-E-201(Top +30) Scrubber Area | 55.6169957,24.9765073 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 135 | 95L-JB326-ST135-122 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1296 | Ashik Kasim | 2023-09-04 05:57 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1297 | 9C8FA64E080104E0 |  | Margham | Area 95 | 95-E-201(Top +30)Near Scrubber Area | 55.6169551,24.976549 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 133 | 95L-JB325-ST133-120 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1297 | Ashik Kasim | 2023-09-04 06:02 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1298 | 372BB64C080104E0 |  | Margham | Area 95 | 95-E-201(Top +30)Near Scrubber Area | 55.617012,24.9766196 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 132 | 95L-JB326-ST132-119 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment unless proven otherwise |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1298 | Ashik Kasim | 2023-09-04 06:10 | A6. Pending A3. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1299 | 032DB64C080104E0 |  | Margham | Area 95 | 95-E-201(Top +45)Near Scrubber Area | 55.6171001,24.9766194 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 159 | 95L-JB327-FL159-146 | Flood Light | Appleton | S-51HPS | GAM771LXR12 | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | Not available | Not Available | +40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1299 | Ashik Kasim | 2023-09-04 06:12 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable
1300 | 8892A64E080104E0 |  | Margham | Area 95 | 95-E-201(Top +45)Near Scrubber Area | 55.6170692,24.9766045 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 147 | 95L-JB341-ST147-134 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment unless proven otherwise |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1300 | Ashik Kasim | 2023-09-04 06:15 | A6. Pending A3. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1301 | 2A2BB64C080104E0 |  | Margham | Area 95 | 95-E-201(Top +45)Near Scrubber Area | 55.617043,24.976579 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 146 | 95L-JB341-ST144-131 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment unless proven otherwise |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1301 | Ashik Kasim | 2023-09-04 06:20 | A6. Pending A3. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1302 | BB91A64E080104E0 |  | Margham | Area 95 | 95-E-201(Top +45)Near Scrubber Area | 55.6170444,24.9765505 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 143 | 95L-JB326-ST143 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available A6. Circuit id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id A6. Fix circuit id |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1302 | Ashik Kasim | 2023-09-04 06:23 | A3. Pending A6. Pending A6. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1303 | 4129B64C080104E0 |  | Margham | Area 95 | 95-E-201(Top +45)Near Scrubber Area | 55.6170125,24.9765698 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 145 | 95L-JB341-ST145-132 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment unless proven otherwise |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1303 | Ashik Kasim | 2023-09-04 06:28 | A6. Pending A3. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1304 | 7691A64E080104E0 |  | Margham | Area 95 | 95-E-201(Top +45)Near Scrubber Area | 55.6170802,24.9765686 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 144 | 95L-JB341-ST146-133 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment unless proven otherwise |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1304 | Ashik Kasim | 2023-09-04 06:32 | A6. Pending A3. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1305 | 9F8CA64E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Skid(Top) | 55.6176376,24.9754267 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-036 | 25-PC-305-A | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040184 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1305 | Ashik Kasim | 2023-09-05 10:40 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1306 | 352DB64C080104E0 |  | Margham | Area 25 | MEC 01 Compressor Skid(Top) | 55.6177317,24.9754554 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-BAL-103 | 25-PC-306 | Flood Light | EATON | FMVA16LCY-UNV1-76-M20 | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 div 2 | Not Available | T4A | Not Available | 60 | UL | Not Available | Not applicable | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1306 | Ashik Kasim | 2023-09-05 10:44 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1307 | 8529B64C080104E0 |  | Margham | Area 25 | MEC 01 Compressor Skid(Top) | 55.6178479,24.9754071 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HBL-103 | 25-PC-280 | LED HIGH BAY LIGHTING, | EATON | NFMVA25LCY/UNV1 76 M20 | Not Available | Electrical | 3 | Gc | IEC | Ex ec | IIC | T4 | Not Available | -40 +55 | DEMKO | DEMKO15ATEX1377X | Yes | Lighting | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Scaffolding |  | Data Sheet 1307 | Ashik Kasim | 2023-09-05 11:10 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Scaffolding
1308 | E92CB64C080104E0 |  | Margham | Area 25 | MEC 01 Compressor Skid(Top) | 55.6178015,24.9754325 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-023 | 25-PC-279 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040289 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1308 | Ashik Kasim | 2023-09-05 11:09 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1309 | F329B64C080104E0 |  | Margham | Area 25 | MEC 01 Compressor Skid(Top) | 55.617856,24.9753591 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HBL-106 | 25-PC-302 | LED HIGH BAY LIGHTING, | EATON | NFMVA25LCY/UNV1 76 M20 | Not Available | Electrical | 3 | Gc | IEC | Ex ec | IIC | T4 | Not Available | -40 +55 | DEMKO | DEMKO15ATEX1377X | Yes | Lighting | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Scaffolding |  | Data Sheet 1309 | Ashik Kasim | 2023-09-05 11:27 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Scaffolding
1310 | 6B8FA64E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Skid(Top) | 55.6178845,24.9753126 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-034 | 25-PC-301 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040059 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1310 | Ashik Kasim | 2023-09-05 11:40 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1311 | 5990A64E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Skid(Top) | 55.6178171,24.9753182 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-037 | 25-PC-307 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040133 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1311 | Ashik Kasim | 2023-09-05 15:34 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1312 | 6692A64E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Skid(Top) | 55.6178024,24.9753293 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-BFL-101 | 25-PC-308 | LED HIGH BAY LIGHTING, | EATON | NFMVA25LCY/UNV1 76 M20 | Not Available | Electrical | 3 | Gc | IEC | Ex ec | IIC | T4 | Not Available | -40 +55 | DEMKO | DEMKO15ATEX1377X | Yes | Lighting | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Scaffolding |  | Data Sheet 1312 | Ashik Kasim | 2023-09-05 15:44 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Scaffolding
1313 | 0C2DB64C080104E0 |  | Margham | Area 25 | MEC 01 Compressor Skid(Top) | 55.6178178,24.9752816 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-022 | 25-PC-277 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040272 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1313 | Ashik Kasim | 2023-09-05 15:56 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1314 | 2B2BB64C080104E0 |  | Margham | Area 25 | MEC 01 Compressor Skid(Top) | 55.6177263,24.9752409 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-BFL-102 | 25-PC-278 | LED HIGH BAY LIGHTING, | EATON | NFMVA25LCY/UNV1 76 M20 | Not Available | Electrical | 3 | Gc | IEC | Ex ec | IIC | T4 | Not Available | -40 +55 | DEMKO | DEMKO15ATEX1377X | Yes | Lighting | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Scaffolding |  | Data Sheet 1314 | Ashik Kasim | 2023-09-05 16:05 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Scaffolding
1315 | 7892A64E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Skid(Top) | 55.6178338,24.9752045 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-022-A | 25-PC-278A | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040056 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1315 | Ashik Kasim | 2023-09-06 09:15 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1316 | 9891A64E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Skid(Top) | 55.6177971,24.9751345 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-BAL-105 | 25-PC-278-B | LED HIGH BAY LIGHTING, | EATON | NFMVA15LCY/UNV1 76 M20 | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T4A | Not Available | +55 | UL | Not Available | Not Applicable | Lighting | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Scaffolding |  | Data Sheet 1316 | Ashik Kasim | 2023-09-06 09:31 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Scaffolding
1317 | 502CB64C080104E0 |  | Margham | Area 25 | MEC 01 Compressor Skid(Top) | 55.6179898,24.9751834 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HBL-105 | 25-PC-300 | LED HIGH BAY LIGHTING, | EATON | NFMVA25LCY/UNV1 76 M20 | Not Available | Electrical | 3 | Gc | IEC | Ex ec | IIC | T4 | Not Available | -40 +55 | DEMKO | DEMKO15ATEX1377X | Yes | Lighting | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Scaffolding |  | Data Sheet 1317 | Ashik Kasim | 2023-09-06 09:46 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Scaffolding
1318 | 6890A64E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Skid(Top) | 55.6180114,24.9751833 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-033 | 25-PC-299 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040279 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1318 | Ashik Kasim | 2023-09-06 09:55 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1319 | 532CB64C080104E0 |  | Margham | Area 25 | MEC 01 Compressor Skid(Top) | 55.6180663,24.9752809 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HBL-102 | 25-PC-282 | LED HIGH BAY LIGHTING, | EATON | NFMVA25LCY/UNV1 76 M20 | Not Available | Electrical | 3 | Gc | IEC | Ex ec | IIC | T4 | Not Available | -40 +55 | DEMKO | DEMKO15ATEX1377X | Yes | Lighting | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Scaffolding |  | Data Sheet 1319 | Ashik Kasim | 2023-09-06 10:38 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Scaffolding
1320 | 3C2BB64C080104E0 |  | Margham | Area 25 | MEC 01 Compressor Skid(Top) | 55.6180379,24.9752983 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-024 | 25-PC-281 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040212 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1320 | Ashik Kasim | 2023-09-06 10:46 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1321 | DA2BB64C080104E0 |  | Margham | Area 25 | MEC 02 Compressor Skid-Near Flame Detector | 55.6178836,24.9750956 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-BAL-203 | 25-PC-488 | LED HIGH BAY LIGHTING, | EATON | NFMVA15LCY/UNV1 76 M20 | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T4A | Not Available | +55 | UL | Not Available | Not Applicable | Lighting | Periodic | e | Close | A6. Equipment id not available | A6. Fix equipment id |  | 1 |  | Yellow | 5 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1321 | Ashik Kasim | 2023-09-06 11:06 | A6. Pending | 1 |  | Yellow | 5 | Minor Repair Required | Equipment Isolation | Scaffolding
1322 | EC91A64E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Skid- Near Flame detector | 55.6179233,24.9750295 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-127 | 25-PC-487-A | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040274 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1322 | Ashik Kasim | 2023-09-06 11:16 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1323 | 962BB64C080104E0 |  | Margham | Area 25 | MEC VSD Transformer-211 | 55.6169283,24.9748071 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-WLF-013 | 25-PC-891 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-025 | Electrical | Not Available | Gc | IEC | Ex db | IIC | T6 | IP66 | -40 ,+55 | NEP | IECEx NEP18.0003X | Yes | Lighting | Periodic | d | Close | A10. Loose glands B6. Broken earth connection | A10. Tighten glands B6. Reinstate connection |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1323 | Ashik Kasim | 2023-09-06 15:50 | A10. Done B6. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-09-07 10:28
1324 | FA2AB64C080104E0 |  | Margham | Area 25 | MEC VSD Transformer-211 | 55.6169401,24.9748097 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-292 | 25-PC-892 | Light Junction Box | Weidmuller | Klippon POK 161609 | XB-AE-A-040384 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECExIBE13.0004X | Yes | Others | Periodic | e | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1324 | Ashik Kasim | 2023-09-06 15:53 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-09-07 08:24
1325 | 192BB64C080104E0 |  | Margham | Area 25 | MEC VSD Transformer-211 | 55.6169521,24.9747946 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-WLF-014 | 25-PC-892 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-085 | Electrical | Not Available | Gc | IEC | Ex db | IIC | T6 | IP66 | -40 ,+55 | NEP | IECEx NEP18.0003X | Yes | Lighting | Periodic | d | Close | B6. Broken earth connection | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1325 | Ashik Kasim | 2023-09-06 15:55 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-09-07 08:22
1326 | CB2AB64C080104E0 |  | Margham | Area 25 | MEC VSD Transformer-211 | 55.6169014,24.9748889 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-WLF-012 | 25-PC-889 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-089 | Electrical | Not Available | Gc | IEC | Ex db | IIC | T6 | IP66 | -40 ,+55 | NEP | IECEx NEP18.0003X | Yes | Lighting | Periodic | d | Close | A10. Loose glands B6. Broken earth connection | A10. Tighten glands B6. Reinstate connection |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1326 | Ashik Kasim | 2023-09-06 16:03 | A10. Done B6. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-09-07 08:34
1327 | E92AB64C080104E0 |  | Margham | Area 25 | MEC VSD Transformer-211 | 55.6169172,24.9748718 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-291 | 25-PC-888 | Light Junction Box | Weidmuller | Klippon POK 161609 | XB-AE-A-040383 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECExIBE13.0004X | Yes | Others | Periodic | e | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1327 | Ashik Kasim | 2023-09-06 16:04 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-09-07 08:58
1328 | 388FA64E080104E0 |  | Margham | Area 25 | MEC VSD Transformer-211 | 55.6169014,24.9748889 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-WLF-011 | 25-PC-888 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-086 | Electrical | Not Available | Gc | IEC | Ex db | IIC | T6 | IP66 | -40 ,+55 | NEP | IECEx NEP18.0003X | Yes | Lighting | Periodic | d | Close | A10. Loose glands B6. Broken earth connection | A10. Tighten glands B6. Reinstate connection |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1328 | Ashik Kasim | 2023-09-06 16:17 | A10. Done B6. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-09-07 08:36
1329 | 872BB64C080104E0 |  | Margham | Area 25 | MEC VSD Transformer-311 | 55.6169796,24.9747029 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-WLF-018 | 25-PC-898 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-035 | Electrical | Not Available | Gc | IEC | Ex db | IIC | T6 | IP66 | -40 ,+55 | NEP | IECEx NEP18.0003X | Yes | Lighting | Periodic | d | Close | A10. Loose glands B6. Broken earth connection | A10. Tighten glands B6. Reinstate connection |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1329 | Ashik Kasim | 2023-09-07 05:37 | A10. Done B6. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-09-07 10:44
1330 | 4591A64E080104E0 |  | Margham | Area 25 | MEC VSD Transformer-311 | 55.616955,24.9746954 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-294 | 25-PC-898 | Light Junction Box | Weidmuller | Klippon POK 161609 | XB-AE-A-040341 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECExIBE13.0004X | Yes | Others | Periodic | e | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1330 | Ashik Kasim | 2023-09-07 05:40 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-09-07 10:45
1331 | 5092A64E080104E0 |  | Margham | Area 25 | MEC VSD Transformer-311 | 55.6169484,24.9747091 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-WLF-017 | 25-PC-897 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-027 | Electrical | Not Available | Gc | IEC | Ex db | IIC | T6 | IP66 | -40 ,+55 | NEP | IECEx NEP18.0003X | Yes | Lighting | Periodic | d | Close | A10. Loose glands B6. Broken earth connection | A10. Tighten glands B6. Reinstate connection |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1331 | Ashik Kasim | 2023-09-07 05:44 | A10. Done B6. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-09-07 10:46
1332 | D92BB64C080104E0 |  | Margham | Area 25 | MEC VSD Transformer-311 | 55.6169248,24.974698 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-249 | 25-PC-743 | Light Junction Box | Weidmuller | Klippon POK 161609 | XB-AE-A-040287 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECExIBE13.0004X | Yes | Others | Periodic | e | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1332 | Ashik Kasim | 2023-09-07 05:47 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-09-07 10:50
1333 | ED90A64E080104E0 |  | Margham | Area 25 | MEC VSD Transformer-311 | 55.6169266,24.9747464 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-WLF-015 | 25-PC-895 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-044 | Electrical | Not Available | Gc | IEC | Ex db | IIC | T6 | IP66 | -40 ,+55 | NEP | IECEx NEP18.0003X | Yes | Lighting | Periodic | d | Close | A10. Loose glands B6. Broken earth connection | A10. Tighten glands B6. Reinstate connection |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1333 | Ashik Kasim | 2023-09-07 05:57 | A10. Done B6. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-09-07 11:07
1334 | 0B91A64E080104E0 |  | Margham | Area 25 | MEC VSD Transformer-311 | 55.6169205,24.9747292 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-293 | 25-PC-893 | Light Junction Box | Weidmuller | Klippon POK 161609 | XB-AE-A-040385 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECExIBE13.0004X | Yes | Others | Periodic | e | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1334 | Ashik Kasim | 2023-09-07 05:59 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-09-07 11:09
1335 | 092BB64C080104E0 |  | Margham | Area 25 | MEC VSD Transformer-311 | 55.6169266,24.9747464 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-WLF-016 | 25-PC-894 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-028 | Electrical | Not Available | Gc | IEC | Ex db | IIC | T6 | IP66 | -40 ,+55 | NEP | IECEx NEP18.0003X | Yes | Lighting | Periodic | d | Close | A10. Loose glands B6. Broken earth connection | A10. Tighten glands B6. Reinstate connection |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1335 | Ashik Kasim | 2023-09-07 06:05 | A10. Done B6. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-09-07 11:11
1336 | 732BB64C080104E0 |  | Margham | Area 25 | MEC VSD Transformer-111 | 55.6169656,24.9748088 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-WLF-009 | 25-PC-885 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-092 | Electrical | Not Available | Gc | IEC | Ex db | IIC | T6 | IP66 | -40 ,+55 | NEP | IECEx NEP18.0003X | Yes | Lighting | Periodic | d | Close | A10. Loose glands B6. Broken earth connection | A10. Tighten glands B6. Reinstate connection |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1336 | Ashik Kasim | 2023-09-07 06:21 | A10. Done B6. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-09-07 11:29
1337 | 352CB64C080104E0 |  | Margham | Area 25 | MEC VSD Transformer-111 | 55.6169669,24.9748246 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-290 | 25-PC-893 | Light Junction Box | Weidmuller | Klippon POK 161609 | XB-AE-A-040382 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECExIBE13.0004X | Yes | Others | Periodic | e | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1337 | Ashik Kasim | 2023-09-07 06:24 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-09-07 11:27
1338 | FD8CA64E080104E0 |  | Margham | Area 25 | MEC VSD Transformer-111 | 55.6169628,24.9748296 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-WLF-010 | 25-PC-886 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-100 | Electrical | Not Available | Gc | IEC | Ex db | IIC | T6 | IP66 | -40 ,+55 | NEP | IECEx NEP18.0003X | Yes | Lighting | Periodic | d | Close | A10. Loose glands B6. Broken earth connection | A10. Tighten glands B6. Reinstate connection |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1338 | Ashik Kasim | 2023-09-07 06:26 | A10. Done B6. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-09-07 11:49
1339 | EFC4AB4E080104E0 |  | Margham | Area 25 | MEC VSD Transformer-111 | 55.6169174,24.9748834 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-WLF-008 | 25-PC-883 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-088 | Electrical | Not Available | Gc | IEC | Ex db | IIC | T6 | IP66 | -40 ,+55 | NEP | IECEx NEP18.0003X | Yes | Lighting | Periodic | d | Close | A10. Loose glands B6. Broken earth connection | A10. Tighten glands B6. Reinstate connection |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1339 | Ashik Kasim | 2023-09-07 06:32 | A10. Done B6. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-09-07 11:40
1340 | 042CB64C080104E0 |  | Margham | Area 25 | MEC VSD Transformer-111 | 55.6169344,24.9748587 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-289 | 25-PC-882 | Light Junction Box | Weidmuller | Klippon POK 161609 | XB-AE-A-040381 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECExIBE13.0004X | Yes | Others | Periodic | e | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1340 | Ashik Kasim | 2023-09-07 06:34 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-09-07 11:42
1341 | D929B64C080104E0 |  | Margham | Area 25 | MEC VSD Transformer-111 | 55.616971,24.9748654 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-WLF-007 | 25-PC-882 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-087 | Electrical | Not Available | Gc | IEC | Ex db | IIC | T6 | IP66 | -40 ,+55 | NEP | IECEx NEP18.0003X | Yes | Lighting | Periodic | d | Close | B6. Broken earth connection | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1341 | Ashik Kasim | 2023-09-07 06:40 | B6. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-09-07 11:48
1342 | F729B64C080104E0 |  | Margham | Area 95 | 95-XV-9701 Area- Stairway | 55.6178982,24.9764992 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 80-ST-610 | 80-ST-602 | Street Light | KILLARK | HPS | VM3S108IR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T2 | Not Available | +55 | CSA | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Temperature class not suitable A3. Ambient temperature not suitable B6. Earth cable not installed | A3. Replace equipment A3. Replace equipment unless proven otherwise B6. Install earth cable |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1342 | Ashik Kasim | 2023-09-08 05:44 | A3. Pending A3. Pending B6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1343 | A88FA64E080104E0 |  | Margham | Area 95 | 95-XV-9701 Area- Stairways -TOP | 55.6177514,24.9766143 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 80-ST-617 | 80-ST-618 | Street Light | KILLARK | HPS | VM3S108IR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T2 | Not Available | +55 | CSA | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Temperature class not suitable A3. Ambient temperature not suitable B6. Earth cable not installed | A3. Replace equipment A3. Replace equipment unless proven otherwise B6. Install earth cable |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1343 | Ashik Kasim | 2023-09-08 05:49 | A3. Pending A3. Pending B6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1344 | 0D2CB64C080104E0 |  | Margham | Area 95 | 95-XV-9701 Area- Stairways -TOP | 55.6177514,24.9766143 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 70-ST-611 | 80-ST-610 | Street Light | KILLARK | HPS | VM3S108IR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T2 | Not Available | +55 | CSA | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Temperature class not suitable A3. Ambient temperature not suitable B6. Earth cable not installed | A3. Replace equipment A3. Replace equipment unless proven otherwise B6. Install earth cable |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1344 | Ashik Kasim | 2023-09-08 05:56 | A3. Pending A3. Pending B6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1345 | A691A64E080104E0 |  | Margham | Area 95 | 95-XV-9701 Area- Stairways -TOP | 55.6179726,24.976618 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 80-ST-618 | Street Light | KILLARK | HPS | VM3S108IR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T2 | Not Available | +55 | CSA | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Temperature class not suitable A3. Ambient temperature not suitable A6. Equipment id not available B6. Earth cable not installed | A3. Replace equipment A3. Replace equipment unless proven otherwise A6. Fix equipment id B6. Install earth cable |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1345 | Ashik Kasim | 2023-09-08 06:02 | A3. Pending A3. Pending A6. Pending B6. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1346 | 698FA64E080104E0 |  | Margham | Area 95 | 95-XV-9701 Area- Stairways -TOP | 55.6179726,24.976618 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 80-ST-618 | 80-ST-617 | Street Light | KILLARK | HPS | VM3S108IR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T2 | Not Available | +55 | CSA | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Temperature class not suitable A3. Ambient temperature not suitable B6. Earth cable not installed | A3. Replace equipment A3. Replace equipment unless proven otherwise B6. Install earth cable |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1346 | Ashik Kasim | 2023-09-08 06:01 | A3. Pending A3. Pending B6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1347 | D529B64C080104E0 |  | Margham | Area 95 | 95-XV-9701 Area- Stairways -TOP | 55.6178412,24.9765962 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 80-ST-610 | Street Light | KILLARK | HPS | VM3S108IR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T2 | Not Available | +55 | CSA | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Temperature class not suitable A3. Ambient temperature not suitable A6. Equipment id not available B6. Earth cable not installed | A3. Replace equipment A3. Replace equipment unless proven otherwise A6. Fix equipment id B6. Install earth cable |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1347 | Ashik Kasim | 2023-09-08 06:03 | A3. Pending A3. Pending A6. Pending B6. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1348 | 732CB64C080104E0 |  | Margham | Area 95 | 95-XV-9701 Area- Stairways -TOP | 55.6178262,24.9766019 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 80-ST-608 | 80-ST-607 | Street Light | KILLARK | HPS | VM3S108IR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T2 | Not Available | +55 | CSA | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Temperature class not suitable A3. Ambient temperature not suitable B6. Earth cable not installed | A3. Replace equipment A3. Replace equipment unless proven otherwise B6. Install earth cable |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1348 | Ashik Kasim | 2023-09-08 06:06 | A3. Pending A3. Pending B6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1349 | 1391A64E080104E0 |  | Margham | Area 95 | 95-XV-9701 Area- Stairways +15 Deck | 55.6178008,24.976603 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 80-ST-616 | 80-ST-615 | Street Light | KILLARK | HPS | VM3S108IR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T2 | Not Available | +55 | CSA | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Temperature class not suitable A3. Ambient temperature not suitable B6. Earth cable not installed | A3. Replace equipment A3. Replace equipment unless proven otherwise B6. Install earth cable |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1349 | Ashik Kasim | 2023-09-08 06:09 | A3. Pending A3. Pending B6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1350 | D62BB64C080104E0 |  | Margham | Area 95 | 95-XV-9700 Area- +15 Deck | 55.6179117,24.9766424 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 80-ST-605 | 80-ST-604 | Street Light | KILLARK | HPS | VM3S108IR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T2 | Not Available | +55 | CSA | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Temperature class not suitable A3. Ambient temperature not suitable B6. Earth cable not installed | A3. Replace equipment A3. Replace equipment unless proven otherwise B6. Install earth cable |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1350 | Ashik Kasim | 2023-09-08 06:12 | A3. Pending A3. Pending B6. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1351 | 2492A64E080104E0 |  | Margham | Area 95 | 95-XV-9700 Area- +15 Deck | 55.6179971,24.9766546 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 80-ST-604 | 80-ST-603 | Street Light | KILLARK | HPS | VM3S108IR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T2 | Not Available | +55 | CSA | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Temperature class not suitable A3. Ambient temperature not suitable B6. Earth cable not installed | A3. Replace equipment A3. Replace equipment unless proven otherwise B6. Install earth cable |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1351 | Ashik Kasim | 2023-09-08 06:18 | A3. Pending A3. Pending B6. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1352 | 7129B64C080104E0 |  | Margham | Area 95 | 95-XV-9700 Area- +15 Deck | 55.618025,24.9766082 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 80-ST-614 | 80-JB601 | Street Light | KILLARK | HPS | VM3S108IR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T2 | Not Available | +55 | CSA | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Temperature class not suitable A3. Ambient temperature not suitable B6. Earth cable not installed | A3. Replace equipment A3. Replace equipment unless proven otherwise B6. Install earth cable |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1352 | Ashik Kasim | 2023-09-08 06:20 | A3. Pending A3. Pending B6. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1353 | D98FA64E080104E0 |  | Margham | Area 95 | 95-XV-9701 Area- +15 Deck | 55.6179014,24.9765789 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 80-ST-615 | 80-ST-614 | Street Light | KILLARK | HPS | VM3S108IR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T2 | Not Available | +55 | CSA | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Temperature class not suitable A3. Ambient temperature not suitable B6. Earth cable not installed | A3. Replace equipment A3. Replace equipment unless proven otherwise B6. Install earth cable |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1353 | Ashik Kasim | 2023-09-08 06:23 | A3. Pending A3. Pending B6. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1354 | 962CB64C080104E0 |  | Margham | Area 95 | 95-XV-9701 Area- +15 Deck | 55.6177864,24.976677 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 80-ST-606 | 80-ST-607 | Street Light | KILLARK | HPS | VM3S108IR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T2 | Not Available | +55 | CSA | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Temperature class not suitable A3. Ambient temperature not suitable B6. Earth cable not installed | A3. Replace equipment A3. Replace equipment unless proven otherwise B6. Install earth cable |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1354 | Ashik Kasim | 2023-09-08 06:24 | A3. Pending A3. Pending B6. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1355 | F191A64E080104E0 |  | Margham | Area 95 | 95-XV-9701 Area- +15 Deck | 55.6178158,24.9766131 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 80-ST-607 | 80-ST-606 | Street Light | KILLARK | HPS | VM3S108IR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T2 | Not Available | +55 | CSA | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Temperature class not suitable A3. Ambient temperature not suitable B6. Earth cable not installed | A3. Replace equipment A3. Replace equipment unless proven otherwise B6. Install earth cable |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1355 | Ashik Kasim | 2023-09-08 06:27 | A3. Pending A3. Pending B6. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1356 | A491A64E080104E0 |  | Margham | Area 25 | MEC 01 Compressor Skid (Cooler Side) | 55.6181875,24.9752377 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-BAL-103 | 25-PC-305B | Flood Light | EATON | FMVA16LCY-UNV1-76-M20 | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 div 2 | Not Available | T4A | Not Available | 60 | UL | Not Available | Not applicable | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1356 | Ashik Kasim | 2023-09-08 08:59 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1357 | 5C29B64C080104E0 |  | Margham | Area 25 | MEC 01 Compressor Skid (Cooler Side) | 55.6180409,24.9752145 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-035-A | 25-PC-305-A | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040165 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1357 | Ashik Kasim | 2023-09-08 09:03 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1358 | 39C2AB4E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Skid (Top) | 55.6178482,24.9747955 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-BAL-205 | 25-PC-460 | Flood Light | EATON | FMVA16LCY-UNV1-76-M20 | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 div 2 | Not Available | T4A | Not Available | 60 | UL | Not Available | Not applicable | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1358 | Ashik Kasim | 2023-09-08 09:25 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1359 | 3E29B64C080104E0 |  | Margham | Area 25 | MEC 02 Compressor Skid (Top) | 55.6178069,24.9748936 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-113 | 25-PC-459 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040073 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1359 | Ashik Kasim | 2023-09-08 09:28 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1360 | 808FA64E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Skid (Top) | 55.6177712,24.9748623 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-BFL-202 | 25-PC-458 | LED HIGH BAY LIGHTING, | EATON | NFMVA15LCY/UNV1 76 M20 | Not Available | Electrical | 3 | Gc | NEC | Class 1 Div 2 | ABCD | T4A | Not Available | -40 +55 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Scaffolding |  | Data Sheet 1360 | Ashik Kasim | 2023-09-08 09:43 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Scaffolding
1361 | 272CB64C080104E0 |  | Margham | Area 25 | MEC 02 Compressor Skid (Top) | 55.6178266,24.9748884 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-112 | 25-PC-457 | Light Junction Box | Weidmuller | Klippon POK 161609 Ex | XB-AE-A-040142 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1361 | Ashik Kasim | 2023-09-08 09:57 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1362 | 8F2BB64C080104E0 |  | Margham | Area 25 | MEC 02 Compressor Skid (Top) | 55.6177919,24.9749213 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HBL-206 | 25-PC-484 | LED HIGH BAY LIGHTING, | EATON | NFMVA25LCY/UNV1 76 M20 | Not Available | Electrical | 3 | Gc | IEC | Ex ec | IIC | T4 | Not Available | -40 +55 | DEMKO | DEMKO15ATEX1377X | Yes | Lighting | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Scaffolding |  | Data Sheet 1362 | Ashik Kasim | 2023-09-08 10:07 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Scaffolding
1363 | B78FA64E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Skid (Top) | 55.6177688,24.974925 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-125 | 25-PC-483 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040078 | Electrical | Not Available | Not Available | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1363 | Ashik Kasim | 2023-09-08 10:23 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1364 | 1591A64E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Skid (Top) | 55.6177781,24.9748832 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-HBL-203 | 25-PC-462 | LED HIGH BAY LIGHTING, | EATON | NFMVA25LCY/UNV1 76 M20 | Not Available | Electrical | 3 | Gc | IEC | Ex ec | IIC | T4 | Not Available | -40 +55 | DEMKO | DEMKO15ATEX1377X | Yes | Lighting | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Scaffolding |  | Data Sheet 1364 | Ashik Kasim | 2023-09-08 10:37 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Scaffolding
1365 | E68FA64E080104E0 |  | Margham | Area 25 | MEC 02 Compressor Skid (Top) | 55.617894,24.9749308 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-114 | 25-PC-461 | Light Junction Box | Weidmuller | Klippon POK 121209 Ex | XB-AE-A-040164 | Electrical | Not Available | Not Available | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECEx IBE 13.0004X | Yes | Others | Periodic | e | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1365 | Ashik Kasim | 2023-09-08 10:52 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1366 | 5192A64E080104E0 |  | Margham | Area 95 | 95-E-201(Top +25)Near Scrubber Area | 55.6171289,24.9764712 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 142 | 95L-JB325-ST139-126 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1366 | Ashik Kasim | 2023-09-11 08:51 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1367 | 3B2CB64C080104E0 |  | Margham | Area 95 | 95-E-201(Top +25)Near Scrubber Area | 55.6171188,24.9764852 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 141 | 95L-JB326-ST141-128 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1367 | Ashik Kasim | 2023-09-11 08:57 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1368 | 342BB64C080104E0 |  | Margham | Area 95 | 95-E-201(Top +25)Near Scrubber Area | 55.6170943,24.9766033 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 140 | 95L-JB325-ST140-127 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1368 | Ashik Kasim | 2023-09-11 09:04 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1369 | 7D8FA64E080104E0 |  | Margham | Area 95 | 95-E-201(Top +25)Near Scrubber Area | 55.617159,24.9766358 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 139 | 95L-JB325-ST140-127 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1369 | Ashik Kasim | 2023-09-11 09:09 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1370 | D229B64C080104E0 |  | Margham | Area 95 | 95-E-201(Top +25)Near Scrubber Area | 55.6170341,24.9765349 | Zone 2 | IIB | T3 | IP65 | EE95-A1-600-01 |  | 95-ZS0-9591 | ZSC-9591 | POSITION SWITCH- Suction Scrubber -9591 | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1370 | Ashik Kasim | 2023-09-11 09:38 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1371 | 4692A64E080104E0 |  | Margham | Area 95 | 95-E-201(Top +25)Near Scrubber Area | 55.6170792,24.9766037 | Zone 2 | IIB | T3 | IP65 | EE95-A1-600-01 |  | 95-XV-9591 | 95-XSV-9591A | Junction Box- Suction Scrubber -9591 | Not Available | Not Available | Not visible | Instrumentation | Not Available | Not Available | IEC | Not Available | Not Available | T5 | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed A1. Non conformant equipment | B6. Install earth cable A1. Replace equipment unless proven otherwise |  | 2 |  | Red | 1 | Major Repair Required | Not Applicable | Not Applicable |  | Data Sheet 1371 | Ashik Kasim | 2023-09-11 09:39 | B6. Pending A1. Pending | 2 |  | Red | 1 | Major Repair Required | Not Applicable | Not Applicable
1372 | 852AB64C080104E0 |  | Margham | Area 95 | 95-E-201(Top +25)Near Scrubber Area | 55.6171026,24.9766082 | Zone 2 | IIB | T3 | IP65 | EE95-A1-600-01 |  | 95-PIT-9545 | 95-PIT-9545 | Pressure Transmitter | Rosemount | 3051S2TG3A3ATTA1JB4D1E5M504015 | 8496100 | Instrumentation | Not Available | Not Available | NEC | CLASS 1 DIV 1 | BCD | T5 | Not Available | -50-+85 | FM | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed A10. Non certified blanking elements installed(need to verify) | B6. Install earth cable A10. Replace with suitable type blanking elements |  | 2 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1372 | Ashik Kasim | 2023-09-11 11:18 | B6. Pending A10. Pending | 2 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable
1373 | D629B64C080104E0 |  | Margham | Area 95 | 95-E-201(Top +25)Near Scrubber Area | 55.6171231,24.9765105 | Zone 2 | IIB | T3 | IP65 | EE95-A1-600-01 |  | 95-PIT-9550 | 95-PIT-9550 | Pressure Transmitter | Rosemount | 3051S2TG3A3ATTA1JB4D1E5M504015 | 8496106 | Instrumentation | Not Available | Not Available | NEC | CLASS 1 DIV 1 | BCD | T5 | Not Available | -50-+85 | FM | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed A10. Non certified blanking elements installed(need to verify) | B6. Install earth cable A10. Replace with suitable type blanking elements |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1373 | Ashik Kasim | 2023-09-11 11:18 | B6. Pending A10. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable
1374 | 132DB64C080104E0 |  | Margham | Area 95 | 95-E-201(Top +30)Near Scrubber Area | 55.6169399,24.9765757 | Zone 2 | IIB | T3 | IP65 | EE95-A1-600-01 |  | 95-ZS0-9551 | ZSC-9551 | POSITION SWITCH- Suction Scrubber -9551 | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close | B6. Earth cable not installed A10. Bolts missing A11. Damaged cover A11. Loose cover A15. Flange joint gaps exceeded permitted value | B6. Install earth cable A10. Fix with manufacture recommended bolts A11. Replace with manufacture type cover A11. Tighten the cover A15. Replace equipment |  | 5 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1374 | Ashik Kasim | 2023-09-11 10:16 | B6. Pending A10. Pending A11. Pending A11. Pending A15. Pending | 5 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable
1375 | F22AB64C080104E0 |  | Margham | Area 95 | 95-E-201(Top +30)Near Scrubber Area | 55.6170481,24.9766349 | Zone 2 | IIB | T3 | IP65 | EE95-A1-600-01 |  | 95-XV-9551 | 95-XSV-9551A | Junction Box- Suction Scrubber -9551 | Not Available | Not Available | Not visible | Instrumentation | Not Available | Not Available | IEC | Not Available | Not Available | T5 | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed A1. Non conformant equipment | B6. Install earth cable A1. Replace equipment unless proven otherwise |  | 2 |  | Red | 1 | Major Repair Required | Not Applicable | Not Applicable |  | Data Sheet 1375 | Ashik Kasim | 2023-09-11 10:18 | B6. Pending A1. Pending | 2 |  | Red | 1 | Major Repair Required | Not Applicable | Not Applicable
1376 | 3C29B64C080104E0 |  | Margham | Area 95 | 95-E-201(Top +30)Near Scrubber Area | 55.6170242,24.9765856 | Zone 2 | IIB | T3 | IP65 | EE95-A1-600-01 |  | 95-XV-9550 | 95-XSV-9550A | Junction Box- Suction Scrubber -9550 | Not Available | Not Available | Not visible | Instrumentation | Not Available | Not Available | IEC | Not Available | Not Available | T5 | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed A1. Non conformant equipment | B6. Install earth cable A1. Replace equipment unless proven otherwise |  | 2 |  | Red | 1 | Major Repair Required | Not Applicable | Not Applicable |  | Data Sheet 1376 | Ashik Kasim | 2023-09-11 10:24 | B6. Pending A1. Pending | 2 |  | Red | 1 | Major Repair Required | Not Applicable | Not Applicable
1377 | 862CB64C080104E0 |  | Margham | Area 95 | 95-E-201(Top +30)Near Scrubber Area | 55.6169399,24.9765757 | Zone 2 | IIB | T3 | IP65 | EE95-A1-600-01 |  | 95-ZS0-9550 | ZSC-9550 | POSITION SWITCH- Suction Scrubber -9550 | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1377 | Ashik Kasim | 2023-09-11 10:30 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding
1378 | 6392A64E080104E0 |  | Margham | Area 95 | 95-E-201(Top +30)Near Scrubber Area | 55.6168891,24.9765648 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-AE/TS-9519 | Not Available | Gas Detector --Switch | Not visible | ED2SC175-UD1-PBGR-UCLP-RESET-A | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 Div 2 | BCD | T6 | IP56 | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed | A6. Fix circuit id B6. Install earth cable |  | 2 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 1378 | Ashik Kasim | 2023-09-11 10:46 | A6. Pending B6. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable
1379 | 752BB64C080104E0 |  | Margham | Area 95 | 95-E-201(Top +30)Near Scrubber Area | 55.6169481,24.9766388 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-AE-9519 | Not Available | IR Flame Detector | Dettronics | X3301A | 19MAY015753 | Instrumentation | Not Available | Not Available | NEC | Class 1 | BCD | T6 | IP66/67 | -40 +60 | FM | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed | A6. Fix circuit id B6. Install earth cable |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1379 | Ashik Kasim | 2023-09-11 11:01 | A6. Pending B6. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1380 | 8491A64E080104E0 |  | Margham | Area 95 | 95-E-201(Top +30)Near Scrubber Area | 55.6169593,24.9765751 | Zone 2 | IIB | T3 | IP65 | EE95-A1-600-01 |  | 95-PDIT-9552 | 95-PDIT-2552 | Pressure Differential Transmitter | Rosemount | 3051S2TG3A3ATTA1JB4D1E5M504015 | 8496113 | Instrumentation | Not Available | Not Available | NEC | CLASS 1 DIV 1 | BCD | T5 | Not Available | -50-+85 | FM | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed A10. Non certified blanking elements installed A10. Wrong type blanking elements installed(loose and only two threads engaged) | B6. Install earth cable A10. Replace with suitable type blanking elements A10. Replace with suitable type blanking elements |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1380 | Ashik Kasim | 2023-09-11 11:15 | B6. Pending A10. Pending A10. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable
1381 | 8B8FA64E080104E0 |  | Margham | Area 95 | 95-E-201(Top +30)Near Scrubber Area | 55.616936,24.9765693 | Zone 2 | IIB | T3 | IP65 | EE95-A1-600-01 |  | 95-PIT-9554 | 95-PIT-9554 | Pressure Transmitter | Rosemount | 3051S2TG3A3ATTA1JB4D1E5M504015 | 8496101 | Instrumentation | Not Available | Not Available | NEC | CLASS 1 DIV 1 | BCD | T5 | Not Available | -50-+85 | FM | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed A10. Non certified blanking elements installed(need to verify) | B6. Install earth cable A10. Replace with suitable type blanking elements |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1381 | Ashik Kasim | 2023-09-11 11:22 | B6. Pending A10. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable
1382 | EE91A64E080104E0 |  | Margham | Area 95 | 95-E-201(Top +30)Near Scrubber Area | 55.6170568,24.9766026 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB325-ST142-129 | Junction Box | Hoffman | Not Available | Not Available | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | e | Close | A6. Equipment id not available A1. Non certified equipment | A6. Fix equipment id A1. Replace equipment |  | 2 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1382 | Ashik Kasim | 2023-09-11 11:38 | A6. Pending A1. Pending | 2 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable
1383 | 7D2CB64C080104E0 |  | Margham | Area 95 | 95-E-201(Top +30)Near Scrubber Area | 55.6170034,24.9765307 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB324-ST138-125 | Junction Box | Hoffman | Not Available | Not Available | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | e | Close | A6. Equipment id not available A1. Non certified equipment | A6. Fix equipment id A1. Replace equipment |  | 2 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1383 | Ashik Kasim | 2023-09-11 11:41 | A6. Pending A1. Pending | 2 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable
1384 | 482CB64C080104E0 |  | Margham | Area 95 | 95-E-201(+15)Scrubber Area | 55.616978,24.9766276 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 138 | 95L-JB324-ST138/125 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1384 | Ashik Kasim | 2023-09-11 15:19 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1385 | C729B64C080104E0 |  | Margham | Area 95 | 95-E-201(+15)Scrubber Area | 55.6168759,24.9765904 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 137 | 95L-JB326-ST137-124 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1385 | Ashik Kasim | 2023-09-11 15:26 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1386 | 9B2AB64C080104E0 |  | Margham | Area 95 | 95-E-201(+15)Scrubber Area | 55.6168973,24.9766555 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-LIT-9563A | 95-LIT-9563A | Level Transmitter | K-TEK | MT5000 | 09-M1349 | Instrumentation | Not Available | Not Available | NEC | Class 1 Div 1 | CD | T4 | Not Available | +77 | FM | Not Available | Not Applicable | Others | Periodic | i | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1386 | Ashik Kasim | 2023-09-11 15:32 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1387 | CE91A64E080104E0 |  | Margham | Area 95 | 95-E-201(+15)Scrubber Area | 55.6169079,24.9766613 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-LIT-9563B | 95-LIT-9563B | Level Transmitter | K-TEK | MT5000 | 09-M1350 | Instrumentation | Not Available | Not Available | NEC | Class 1 Div 1 | CD | T4 | Not Available | +77 | FM | Not Available | Not Applicable | Others | Periodic | i | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1387 | Ashik Kasim | 2023-09-11 15:34 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1388 | 152DB64C080104E0 |  | Margham | Area 95 | 95-E-201(+15)Scrubber Area | 55.6168686,24.9766134 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-LIT-9562 | 95-LIT-9562 | Level Transmitter | K-TEK | MT5000 | 09-M1350 | Instrumentation | Not Available | Not Available | NEC | Class 1 Div 1 | CD | T4 | Not Available | +77 | FM | Not Available | Not Applicable | Others | Periodic | i | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1388 | Ashik Kasim | 2023-09-11 15:36 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1389 | 6B2CB64C080104E0 |  | Margham | Area 95 | 95-E-201(+15)Scrubber Area | 55.6168748,24.9766349 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-LIT-9561 | 95-LIT-9561 | Level Transmitter | K-TEK | MT5000 | 09-M1350 | Instrumentation | Not Available | Not Available | NEC | Class 1 Div 1 | CD | T4 | Not Available | +77 | FM | Not Available | Not Applicable | Others | Periodic | i | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1389 | Ashik Kasim | 2023-09-11 15:39 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1390 | 5A93A64E080104E0 |  | Margham | Area 95 | 95-E-201(+25)Scrubber Area | 55.6169261,24.9766051 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 135 | 95L-JB326-ST136-123 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1390 | Ashik Kasim | 2023-09-11 15:54 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1391 | 1C2DB64C080104E0 |  | Margham | Area 95 | 95-E-201(Top +45)Pipe Rack | 55.6171289,24.9764712 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 150 | 95L-JB341-ST1#0-137 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment unless proven otherwise |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1391 | Ashik Kasim | 2023-09-12 07:51 | A6. Pending A3. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1392 | 9E29B64C080104E0 |  | Margham | Area 95 | 95-E-201(Top +45)Pipe Rack | 55.6173718,24.976609 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 341 | 95L-708-JB341 | Junction Box | Hoffman | Not Available | Not Available | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | e | Close | A6. Equipment id not available A1. Non certified equipment | A6. Fix equipment id A1. Replace equipment |  | 2 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1392 | Ashik Kasim | 2023-09-12 07:49 | A6. Pending A1. Pending | 2 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable
1393 | 1C2BB64C080104E0 |  | Margham | Area 95 | 95-E-201(Top +45)Pipe Rack | 55.6172971,24.9765397 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 157 | 95L-JB326-ST157-144 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment unless proven otherwise |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1393 | Ashik Kasim | 2023-09-12 07:57 | A6. Pending A3. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1394 | 9791A64E080104E0 |  | Margham | Area 95 | 95-E-201(Top +70)Pipe Rack | 55.6173117,24.9765484 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 151 | 95L-JB341-ST50-139 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment unless proven otherwise |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1394 | Ashik Kasim | 2023-09-12 08:05 | A6. Pending A3. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1395 | 858FA64E080104E0 |  | Margham | Area 95 | 95-E-201(Top +70)Pipe Rack | 55.6173452,24.9765764 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 155 | 95L-JB327-FL154-141 | Flood Light | Appleton | S-51HPS | GAM771LXR12 | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | Not available | Not Available | +40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A3. Ambient temperature not suitable A6. Equipment id not available | A3. Replace equipment unless proven otherwise A6. Fix equipment id |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1395 | Ashik Kasim | 2023-09-12 08:04 | A3. Pending A6. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable
1396 | 2A92A64E080104E0 |  | Margham | Area 95 | 95-E-201(Top +70)Pipe Rack | 55.6173133,24.9765615 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 145 | 95L-JB326-ST148-135 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment unless proven otherwise |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1396 | Ashik Kasim | 2023-09-12 08:09 | A6. Pending A3. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1397 | C12BB64C080104E0 |  | Margham | Area 95 | 95-E-201(Top +70)Pipe Rack | 55.6172577,24.9765428 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 152 | 95L-JB341-ST149-136 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment unless proven otherwise |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1397 | Ashik Kasim | 2023-09-12 08:11 | A6. Pending A3. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1398 | C890A64E080104E0 |  | Margham | Area 95 | 95-E-201(Top +70)Pipe Rack | 55.6172086,24.9765191 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 149 | 95L-JB341-ST149-136 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment unless proven otherwise |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1398 | Ashik Kasim | 2023-09-12 08:15 | A6. Pending A3. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1399 | AC29B64C080104E0 |  | Margham | Area 95 | 95-E-201(Top +70)Pipe Rack | 55.6172277,24.9765904 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 153 | 95L-JB341-ST153-140 | Street Light | Appleton | S-54 | KPB100LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment unless proven otherwise |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1399 | Ashik Kasim | 2023-09-12 08:17 | A6. Pending A3. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1400 | E291A64E080104E0 |  | Margham | Area 95 | 95-E-201(Top +70)Pipe Rack | 55.6172515,24.9765814 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-PY-9545 | 95-PY-9545 | Positioner- Booster Compressor -Suction Header valve | Masoneilan | SVI-II | Not visible | Instrumentation | Not Available | Not Available | NEC | Not visible | Not visible | Not available | IP66 | -50+85 | Not visible | Not visible | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1400 | Ashik Kasim | 2023-09-12 08:32 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1401 | 5C90A64E080104E0 |  | Margham | Area 95 | 95-E-201(Top +30)Near Scrubber Area | 55.6169994,24.9765182 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-XSV-9596A | Not Available | Solenoid Valve - Booster Compressor Fast Stop Valve | ASCO Red Hat | Not visible | Not visible | Electrical | Not Available | Not Available | NEC | Class 1 Div 1 | ABCD | Not available | Not Available | Not visible | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available | A6. Fix circuit id |  | 1 |  | Yellow | 5 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1401 | Ashik Kasim | 2023-09-12 09:09 | A6. Pending | 1 |  | Yellow | 5 | Minor Repair Required | Equipment Isolation | Not Applicable
1402 | 5B92A64E080104E0 |  | Margham | Area 95 | 95-E-201(Top +30)Near Scrubber Area | 55.6170007,24.9765434 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-XSV-9596B | Not Available | Solenoid Valve - Booster Compressor Fast Stop Valve | ASCO Red Hat | Not visible | Not visible | Electrical | Not Available | Not Available | NEC | Class 1 Div 1 | ABCD | Not available | Not Available | Not visible | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available C1. Non-compliance with environmental conditions A9. Damaged equipment | A6. Fix circuit id C1. Relocate or safeguard the equipment A9. Replace equipment |  | 3 |  | Red | 1 | Replacement Required | Equipment Isolation | Scaffolding |  | Data Sheet 1402 | Ashik Kasim | 2023-09-12 09:36 | A6. Pending C1. Pending A9. Pending | 3 |  | Red | 1 | Replacement Required | Equipment Isolation | Scaffolding
1403 | DCF9A64E080104E0 |  | Margham | Area 95 | 95-E-201(Top +30)Near Scrubber Area | 55.6169773,24.9766006 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-ZSO-9596/95-ZSC-9596 | 95-ZSO-9596 | Position switch | WESTLOCK | Not Available | Not visible | Instrumentation | Not Available | Not Available | NEC | Class 1 | BCD | Not available | Not Available | Not Available | CSA | Not visible | Not Applicable | Others | Periodic | d | Close | A10. Wrong type blanking elements installed(plastic cap used) B6. Earth cable not installed | A10. Replace with suitable type blanking elements B6. Install earth cable |  | 2 |  | Red | 1 | Major Repair Required | Normal Operations | Not Applicable |  | Data Sheet 1403 | Ashik Kasim | 2023-09-12 09:32 | A10. Pending B6. Pending | 2 |  | Red | 1 | Major Repair Required | Normal Operations | Not Applicable
1404 | A891A64E080104E0 |  | Margham | Area 95 | 95-E-201(Top +30)Near Scrubber Area | 55.6169994,24.9765182 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-XSV-95501A | 95-XSV-95501A | Solenoid Valve - Scrubber Spil Back | ASCO Red Hat | Not visible | Not visible | Electrical | Not Available | Not Available | NEC | Class 1 Div 1 | ABCD | Not available | Not Available | Not visible | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1404 | Ashik Kasim | 2023-09-12 09:45 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1405 | AE2AB64C080104E0 |  | Margham | Area 95 | 95-E-201(Top +30)Near Scrubber Area | 55.6169781,24.976542 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-XSV-95501B | 95-XSV-95501B | Solenoid Valve - Scrubber Spil Back | ASCO Red Hat | Not visible | Not visible | Electrical | Not Available | Not Available | NEC | Class 1 Div 1 | ABCD | Not available | Not Available | Not visible | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed A6. Circuit id not available | B6. Install earth cable A6. Fix circuit id |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1405 | Ashik Kasim | 2023-09-12 09:47 | B6. Pending A6. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1406 | 992CB64C080104E0 |  | Margham | Area 95 | 95-E-201(Top +30)Near Scrubber Area | 55.617037,24.9765041 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-FY-9550 | 95-FY-9550 | Positioner- Booster Compressor -Suction Header valve | Masoneilan | SVI-II | Not visible | Instrumentation | Not Available | Not Available | NEC | Not visible | Not visible | Not available | IP66 | -50+85 | Not visible | Not visible | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed A6. Circuit id not available | B6. Install earth cable A6. Fix circuit id |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1406 | Ashik Kasim | 2023-09-12 09:55 | B6. Pending A6. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1407 | F42BB64C080104E0 |  | Margham | Area 95 | 95-E-201(Top +45)Near Discharge Gas Cooler | 55.6170018,24.9765681 | Zone 2 | IIB | T3 | IP65 | EE95-A1-600-01 |  | 95-ZS0-9590 | 95-ZSO-9590 | POSITION SWITCH- Discharge Gas Cooler-9590 | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1407 | Ashik Kasim | 2023-09-12 10:06 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding
1408 | FD90A64E080104E0 |  | Margham | Area 95 | 95-E-201(Top +45)Near Discharge Gas Cooler | 55.6170358,24.9765628 | Zone 2 | IIB | T3 | IP65 | EE95-A1-600-01 |  | 95-XV-9590 | 95-XSV-9590 | Junction Box- Discharge Gas Cooler | Not Available | Not Available | Not visible | Instrumentation | Not Available | Not Available | IEC | Not Available | Not Available | T5 | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed A1. Non conformant equipment | B6. Install earth cable A1. Replace equipment unless proven otherwise |  | 2 |  | Red | 1 | Major Repair Required | Not Applicable | Not Applicable |  | Data Sheet 1408 | Ashik Kasim | 2023-09-12 10:10 | B6. Pending A1. Pending | 2 |  | Red | 1 | Major Repair Required | Not Applicable | Not Applicable
1409 | 9F2CB64C080104E0 |  | Margham | Area 95 | 95-E-201(Top +30)Near Scrubber Area | 55.6171316,24.9765065 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 327 | 95L-JB321-JB327-218 | Junction Box | Hoffman | Not Available | Not Available | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | e | Close | A6. Equipment id not available A1. Non certified equipment | A6. Fix equipment id A1. Replace equipment |  | 2 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1409 | Ashik Kasim | 2023-09-12 10:22 | A6. Pending A1. Pending | 2 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable
1410 | CB2BB64C080104E0 |  | Margham | Area 95 | 95-E-201(Top +30)Near Scrubber Area | 55.6170518,24.9765024 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 326 | 95L-JB322-124-JB326-217 | Junction Box | Hoffman | Not Available | Not Available | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | e | Close | A6. Equipment id not available A1. Non certified equipment | A6. Fix equipment id A1. Replace equipment |  | 2 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1410 | Ashik Kasim | 2023-09-12 10:25 | A6. Pending A1. Pending | 2 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable
1411 | CB2CB64C080104E0 |  | Margham | Area 95 | 95-E-201(Top +30)Near Gas Cooler Fan Area | 55.6170778,24.9765079 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-AE/TS-9518 | Not Available | Flame Detector --Switch | Not visible | ED2SC175-UD1-PBGR-UCLP-RESET-A | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 Div 2 | BCD | T6 | IP56 | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed | A6. Fix circuit id B6. Install earth cable |  | 2 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 1411 | Ashik Kasim | 2023-09-12 10:32 | A6. Pending B6. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable
1412 | 8D2CB64C080104E0 |  | Margham | Area 95 | 95-E-201(Top +30)Near Gas Cooler Fan Area | 55.6170911,24.9765459 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-AE-9518 | Not Available | IR Flame Detector | Dettronics | X3301A | 19MAY015753 | Instrumentation | Not Available | Not Available | NEC | Class 1 | BCD | T6 | IP66/67 | -40 +60 | FM | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed A6. Equipment id not available A6. Circuit id not available | B6. Install earth cable A6. Fix equipment id A6. Fix circuit id |  | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1412 | Ashik Kasim | 2023-09-12 10:35 | B6. Pending A6. Pending A6. Pending | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1413 | 3A2DB64C080104E0 |  | Margham | Area 95 | Discharge Gas Cooler- 95-E-201(Top +30) | 55.6170381,24.9764094 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-AE-9539 | Not Available | Gas Detector | Drager | PIR 7000 | IDS0101 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T4 | IP65 | -40 +80 | PTB | PTB07ATEX06 | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed | A6. Fix circuit id B6. Install earth cable |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1413 | Ashik Kasim | 2023-09-12 10:47 | A6. Pending B6. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1414 | B12AB64C080104E0 |  | Margham | Area 95 | Discharge Gas Cooler- 95-E-201(Top +30) | 55.6170455,24.9763836 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-TY-9574A | 95-TY-9574A | IP Converter | Masoneilan Dresser | 7000 | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T3B | Not Available | -40 +85 | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 1414 | Ashik Kasim | 2023-09-12 10:55 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable
1415 | 372CB64C080104E0 |  | Margham | Area 95 | Discharge Gas Cooler- 95-E-201(Top +30) | 55.6170425,24.9764311 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-TY-9574B | 95-TY-9574B | IP Converter | Masoneilan Dresser | 7000 | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T3B | Not Available | -40 +85 | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 1415 | Ashik Kasim | 2023-09-12 10:58 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable
1416 | 4C8FA64E080104E0 |  | Margham | Area 95 | Discharge Gas Cooler- 95-E-201(Top +30) | 55.6170541,24.9764566 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-TY-9574C | 95-TY-9574C | IP Converter | Masoneilan Dresser | 7000 | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T3B | Not Available | -40 +85 | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 1416 | Ashik Kasim | 2023-09-12 11:01 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable
1417 | 1B2BB64C080104E0 |  | Margham | Area 95 | Discharge Gas Cooler- 95-E-201(Top +30) | 55.6170631,24.9765038 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-TY-9574D | 95-TY-9574D | IP Converter | Masoneilan Dresser | 7000 | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T3B | Not Available | -40 +85 | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 1417 | Ashik Kasim | 2023-09-12 11:05 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable
1418 | 4E2BB64C080104E0 |  | Margham | Area 10 | Gas cooler Area- Ground | 55.6190324,24.9763311 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-E-107B-MA | Not Available | LCS-10-E-107B-MA | Killark | Not visible | Not visible | Electrical | Not Available | Not Available | NEC | Class 1 | D | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available A7. Damaged gasket(need to verify) A10. Multiple adaptors/reducers used along with breather B6. Earth cable not installed C2. Accumulation of dust and dirt B3. Wall openings not sealed properly(conduit seal not Available) | A6. Fix circuit id A7. Replace with manufacture recommended gasket A10. Remove reducer along with breather B6. Install earth cable C2. Remove the dust and dirt B3. Apply sand seals or mortar |  | 6 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1418 | Ashik Kasim | 2023-09-12 16:12 | A6. Pending A7. Pending A10. Pending B6. Pending C2. Pending B3. Pending | 6 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1419 | D52AB64C080104E0 |  | Margham | Area 10 | Gas cooler Area- Ground | 55.6190075,24.9763669 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-E-107B-MB | Not Available | LCS-10-E-107B-MB | Killark | Not visible | Not visible | Electrical | Not Available | Not Available | NEC | Class 1 | D | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available A10. Multiple adaptors/reducers used along with breather B6. Earth cable not installed C2. Accumulation of dust and dirt B3. Wall openings not sealed properly(conduit seal not Available) | A6. Fix circuit id A10. Remove reducer along with breather B6. Install earth cable C2. Remove the dust and dirt B3. Apply sand seals or mortar |  | 5 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1419 | Ashik Kasim | 2023-09-12 16:14 | A6. Pending A10. Pending B6. Pending C2. Pending B3. Pending | 5 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1420 | E22CB64C080104E0 |  | Margham | Area 10 | Gas cooler Area- Ground | 55.6189688,24.9763037 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-E-107A-MA | Not Available | LCS-10-E-107A-MA | Killark | Not visible | Not visible | Electrical | Not Available | Not Available | NEC | Class 1 | D | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available A10. Multiple adaptors/reducers used along with breather B6. Earth cable not installed C2. Accumulation of dust and dirt B3. Wall openings not sealed properly(conduit seal not Available) | A6. Fix circuit id A10. Remove reducer along with breather B6. Install earth cable C2. Remove the dust and dirt B3. Apply sand seals or mortar |  | 5 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1420 | Ashik Kasim | 2023-09-12 16:16 | A6. Pending A10. Pending B6. Pending C2. Pending B3. Pending | 5 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1421 | 7491A64E080104E0 |  | Margham | Area 10 | Gas cooler Area- Ground | 55.6189958,24.9763331 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-E-107A-MB | Not Available | LCS-10-E-107A-MB | Killark | Not visible | Not visible | Electrical | Not Available | Not Available | NEC | Class 1 | D | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available A7. Damaged gasket(need to verify) A10. Multiple adaptors/reducers used along with breather B6. Earth cable not installed C2. Accumulation of dust and dirt B3. Wall openings not sealed properly(conduit seal not Available) | A6. Fix circuit id A7. Replace with manufacture recommended gasket A10. Remove reducer along with breather B6. Install earth cable C2. Remove the dust and dirt B3. Apply sand seals or mortar |  | 6 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1421 | Ashik Kasim | 2023-09-12 16:21 | A6. Pending A7. Pending A10. Pending B6. Pending C2. Pending B3. Pending | 6 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1422 | AB8FA64E080104E0 |  | Margham | Area 10 | Discharge Gas Cooler -Ground | 55.6195373,24.9782916 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-E-109A-MB | Not Available | LCS- 10-E-109A-MB | killark | Not visible | Not visible | Electrical | Not Available | Not Available | NEC | Class 1 | D | T3 | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available A7. Damaged gasket(need to verify) A10. Multiple adaptors/reducers used along with breather B3. Trunking, ducts or pipes not sealed properly(conduit seal not installed) B6. Earth cable not installed | A6. Fix circuit id A7. Replace with manufacture recommended gasket A10. Replace with correct size breather/ stop plug B3. Apply sealing compound or device B6. Install earth cable |  | 5 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1422 | Ashik Kasim | 2023-09-13 08:33 | A6. Pending A7. Pending A10. Pending B3. Pending B6. Pending | 5 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1423 | 4E8FA64E080104E0 |  | Margham | Area 10 | Discharge Gas Cooler -Ground | 55.6190188,24.9762955 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-E-109A-MA | Not Available | LCS- 10-E-109A-MA | killark | FXCS-0B4U-LO | Not visible | Electrical | Not Available | Not Available | NEC | Class 1 | CD | T3 | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available A10. Multiple adaptors/reducers used along with breather B3. Trunking, ducts or pipes not sealed properly(conduit seal not installed) B6. Earth cable not installed | A6. Fix circuit id A10. Replace with correct size breather/ stop plug B3. Apply sealing compound or device B6. Install earth cable |  | 4 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1423 | Ashik Kasim | 2023-09-13 08:39 | A6. Pending A10. Pending B3. Pending B6. Pending | 4 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1424 | 4B29B64C080104E0 |  | Margham | Area 10 | Discharge Gas Cooler -Ground | 55.6190063,24.9763701 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-E-108A-MB | Not Available | LCS- 10-E-108A-MB | killark | Not visible | Not visible | Electrical | Not Available | Not Available | NEC | Class 1 | D | T3 | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available A10. Multiple adaptors/reducers used along with breather B3. Trunking, ducts or pipes not sealed properly(conduit seal not installed) B6. Earth cable not installed A7. Damaged gasket(need to verify) | A6. Fix circuit id A10. Replace with correct size breather/ stop plug B3. Apply sealing compound or device B6. Install earth cable A7. Replace with manufacture recommended gasket |  | 5 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1424 | Ashik Kasim | 2023-09-13 08:42 | A6. Pending A10. Pending B3. Pending B6. Pending A7. Pending | 5 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1425 | 012BB64C080104E0 |  | Margham | Area 10 | Discharge Gas Cooler -Ground | 55.6190063,24.9763701 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-E-108A-MA | Not Available | LCS- 10-E-108A-MA | killark | Not visible | Not visible | Electrical | Not Available | Not Available | NEC | Class 1 | D | T3 | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available A10. Multiple adaptors/reducers used along with breather B3. Trunking, ducts or pipes not sealed properly(conduit seal not installed) B6. Earth cable not installed A7. Damaged gasket(need to verify) | A6. Fix circuit id A10. Replace with correct size breather/ stop plug B3. Apply sealing compound or device B6. Install earth cable A7. Replace with manufacture recommended gasket |  | 5 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1425 | Ashik Kasim | 2023-09-13 08:44 | A6. Pending A10. Pending B3. Pending B6. Pending A7. Pending | 5 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1426 | 9B2CB64C080104E0 |  | Margham | Area 10 | Discharge Gas Cooler -Ground | 55.619009,24.9763914 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-E-108A-MA | Not Available | LCS- 10-E-108A-MA | killark | FXCS-0S3C5 | 0313 | Electrical | Not Available | Not Available | NEC | Class 1 | CD | T3 | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available A10. Multiple adaptors/reducers used along with breather B3. Trunking, ducts or pipes not sealed properly(conduit seal not installed) B6. Earth cable not installed A7. Damaged gasket(need to verify) | A6. Fix circuit id A10. Replace with correct size breather/ stop plug B3. Apply sealing compound or device B6. Install earth cable A7. Replace with manufacture recommended gasket |  | 5 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1426 | Ashik Kasim | 2023-09-13 08:46 | A6. Pending A10. Pending B3. Pending B6. Pending A7. Pending | 5 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1427 | A529B64C080104E0 |  | Margham | Area 10 | Discharge Gas Cooler -Ground | 55.6189877,24.976372 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-E-108B-MA | Not Available | LCS- 10-E-108B-MA | killark | Not visible | Not visible | Electrical | Not Available | Not Available | NEC | Class 1 | CD | T3 | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available A10. Multiple adaptors/reducers used along with breather B3. Trunking, ducts or pipes not sealed properly(conduit seal not installed) B6. Earth cable not installed | A6. Fix circuit id A10. Replace with correct size breather/ stop plug B3. Apply sealing compound or device B6. Install earth cable |  | 4 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1427 | Ashik Kasim | 2023-09-13 08:51 | A6. Pending A10. Pending B3. Pending B6. Pending | 4 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1428 | FC2BB64C080104E0 |  | Margham | Area 10 | Discharge Gas Cooler -Ground | 55.6190318,24.9764861 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-E-108C-MB | Not Available | LCS- 10-E-108C-MB | killark | 0214 | Not visible | Electrical | Not Available | Not Available | NEC | Class 1 | CD | T3 | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available A10. Multiple adaptors/reducers used along with breather B3. Trunking, ducts or pipes not sealed properly(conduit seal not installed) B6. Earth cable not installed | A6. Fix circuit id A10. Replace with correct size breather/ stop plug B3. Apply sealing compound or device B6. Install earth cable |  | 4 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1428 | Ashik Kasim | 2023-09-13 09:01 | A6. Pending A10. Pending B3. Pending B6. Pending | 4 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1429 | 222CB64C080104E0 |  | Margham | Area 10 | Discharge Gas Cooler -Ground | 55.619035,24.9764941 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-E-108C-MA | Not Available | LCS- 10-E-108C-MA | killark | 0214 | Not visible | Electrical | Not Available | Not Available | NEC | Class 1 | CD | T3 | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available A10. Multiple adaptors/reducers used along with breather B3. Trunking, ducts or pipes not sealed properly(conduit seal not installed) B6. Earth cable not installed | A6. Fix circuit id A10. Replace with correct size breather/ stop plug B3. Apply sealing compound or device B6. Install earth cable |  | 4 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1429 | Ashik Kasim | 2023-09-13 09:01 | A6. Pending A10. Pending B3. Pending B6. Pending | 4 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1430 | F090A64E080104E0 |  | Margham | Area 10 | Discharge Gas Cooler -Ground | 55.6189798,24.9765627 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-E-108D-MB | Not Available | LCS- 10-E-108D-MB | killark | 0214 | Not visible | Electrical | Not Available | Not Available | NEC | Class 1 | CD | T3 | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available A10. Multiple adaptors/reducers used along with breather B3. Trunking, ducts or pipes not sealed properly(conduit seal not installed) B6. Earth cable not installed | A6. Fix circuit id A10. Replace with correct size breather/ stop plug B3. Apply sealing compound or device B6. Install earth cable |  | 4 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1430 | Ashik Kasim | 2023-09-13 09:03 | A6. Pending A10. Pending B3. Pending B6. Pending | 4 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1431 | 0B90A64E080104E0 |  | Margham | Area 10 | Discharge Gas Cooler -Ground | 55.618985,24.9765694 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-E-108D-MA | Not Available | LCS- 10-E-108D-MA | killark | Not visible | Not visible | Electrical | Not Available | Not Available | NEC | Class 1 | D | T3 | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available A10. Multiple adaptors/reducers used along with breather B3. Trunking, ducts or pipes not sealed properly(conduit seal not installed) B6. Earth cable not installed | A6. Fix circuit id A10. Replace with correct size breather/ stop plug B3. Apply sealing compound or device B6. Install earth cable |  | 4 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1431 | Ashik Kasim | 2023-09-13 09:05 | A6. Pending A10. Pending B3. Pending B6. Pending | 4 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1432 | A08FA64E080104E0 |  | Margham | Area 10 | Methanol Injection Skid | 55.6187446,24.9764526 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-P-104B |  | Methanol Injection pump motor | WEG | W22 | 1019785426 | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T2 | IP55 | +60 | CSA | Not Available | Not Applicable | Motor | Periodic | e | Close | A6. Circuit id not available A3. Temperature class not available B6. Earth cable not installed | A6. Fix circuit id A3. Certification/data sheet to be reviewed B6. Install earth cable |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1432 | Ashik Kasim | 2023-09-13 09:43 | A6. Pending A3. Pending B6. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable
1433 | C691A64E080104E0 |  | Margham | Area 10 | Methanol Injection Skid | 55.6186931,24.9765079 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-P-104E |  | Methanol Injection motor | Elektrim | ESG | 028461 | Electrical | Not Available | Not Available | Not Applicable | Not Available | Not Available | Not Applicable | Not Available | 40 | CSA | Not Available | Not Applicable | Motor | Periodic | e | Close | A6. Circuit id not available B6. Earth cable not installed A1. Ex data not available A3. Ambient temperature not suitable | A6. Fix circuit id B6. Install earth cable A1. Replace equipment unless proven otherwise A3. Replace equipment unless proven otherwise |  | 4 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1433 | Ashik Kasim | 2023-09-13 10:34 | A6. Pending B6. Pending A1. Pending A3. Pending | 4 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable
1434 | 3B90A64E080104E0 |  | Margham | Area 10 | Methanol Injection Skid | 55.6187117,24.9765334 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-P-104E |  | LCS- Methanol Injection pump motor | Killark | 0402 | FXCS-0B4 U | Electrical | Not Available | Not Available | NEC | Class 1 | CD | Not Applicable | Not Available | Not Available | CSA | Not Available | Not Applicable | Motor | Periodic | e | Close | A6. Circuit id not available B6. Earth cable not installed | A6. Fix circuit id B6. Install earth cable |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1434 | Ashik Kasim | 2023-09-13 10:29 | A6. Pending B6. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1435 | F229B64C080104E0 |  | Margham | Area 10 | Methanol Injection Skid | 55.6186555,24.9765465 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-P-104B |  | LCS- Methanol Injection pump motor | Killark | Not Available | FXCS-0B4 U-LO | Electrical | Not Available | Not Available | NEC | Class 1 | CD | Not Applicable | Not Available | Not Available | CSA | Not Available | Not Applicable | Motor | Periodic | e | Close | A6. Circuit id not available B6. Earth cable not installed A7. Damaged gasket(need to verify) | A6. Fix circuit id B6. Install earth cable A7. Replace with manufacture recommended gasket |  | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1435 | Ashik Kasim | 2023-09-13 10:38 | A6. Pending B6. Pending A7. Pending | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1436 | 7193A64E080104E0 |  | Margham | Area 10 | Condensate Handling Area | 55.6186999,24.976422 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-P-105A | 10-P220 | Booster pump motor | US Electrical Motor | Not Available | 618712 | Electrical | Not Available | Not Available | NEC | Class 1 | D | T3 | Not Available | Not Available | Not Available | Not Available | Not Applicable | Motor | Periodic | d | Close | A10. Multiple adaptors/reducers used | A10. Replace with single adaptor/reducer |  | 1 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1436 | Ashik Kasim | 2023-09-13 11:03 | A10. Pending | 1 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1437 | FE2BB64C080104E0 |  | Margham | Area 10 | Condensate Handling Area | 55.6187271,24.976445 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-P-105B | 10-P227 | Booster pump motor | US Electrical Motor | Not Available | 618712 | Electrical | Not Available | Not Available | NEC | Class 1 | D | T3 | Not Available | Not Available | Not Available | Not Available | Not Applicable | Motor | Periodic | d | Close | A10. Multiple adaptors/reducers used | A10. Replace with single adaptor/reducer |  | 1 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1437 | Ashik Kasim | 2023-09-13 11:08 | A10. Pending | 1 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1438 | AF2CB64C080104E0 |  | Margham | Area 10 | Condensate Handling Area | 55.6187092,24.9764404 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | MCS-10-P-105A | 10-C221 | LCS-Booster pump motor | CEAG | GHG 434 0004 L9001 | Not Available | Electrical | 2 | Not Available | IEC | Ex de | IIC | T6 | IP66 | Not Available | PTB | PTB 00 ATEX 3117 | Not Applicable | Motor | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1438 | Ashik Kasim | 2023-09-13 11:20 | A3. Pending B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1439 | 5E29B64C080104E0 |  | Margham | Area 10 | Condensate Handling Area | 55.6187297,24.9763999 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | MCS-10-P-105B | 10-C228 | LCS-Booster pump motor | CEAG | GHG 434 0004 L9001 | Not Available | Electrical | 2 | Not Available | IEC | Ex de | IIC | T6 | IP66 | Not Available | PTB | PTB 00 ATEX 3117 | Not Applicable | Motor | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1439 | Ashik Kasim | 2023-09-13 11:28 | A3. Pending B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1440 | 632CB64C080104E0 |  | Margham | Area 10 | Discharge Gas Cooler Skid | 55.6193715,24.9762842 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-E-108AMB | Not Available | Inlet Vapour Cooler Fan 10 | Not visible | Not Available | Not visible | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | A1. Ex data not available A6. Circuit id not available B6. Earth cable not installed | A1. Replace equipment unless proven otherwise A6. Fix circuit id B6. Install earth cable |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1440 | Ashik Kasim | 2023-09-13 15:58 | A1. Pending A6. Pending B6. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1441 | E129B64C080104E0 |  | Margham | Area 10 | Discharge Gas Cooler Skid | 55.6193266,24.9766488 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | Not Available | Not Available | Vibration switch -10-E-108A-MB | Frank W Murphy | VS-2-EX | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available B6. Earth cable not installed | A6. Fix equipment id A6. Fix circuit id B6. Install earth cable |  | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1441 | Ashik Kasim | 2023-09-13 16:06 | A6. Pending A6. Pending B6. Pending | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1442 | ED8FA64E080104E0 |  | Margham | Area 10 | Discharge Gas Cooler Skid | 55.6193473,24.9765638 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-E-108B-MB | Not Available | Inlet Vapour Cooler Fan 11 | Not visible | Not Available | Not visible | Instrumentation | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | A1. Ex data not available A6. Circuit id not available B6. Earth cable not installed A15. Flange joint gaps exceeded permitted value | A1. Replace equipment unless proven otherwise A6. Fix circuit id B6. Install earth cable A15. Repair equipment by maintaining the IP |  | 4 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1442 | Ashik Kasim | 2023-09-13 16:10 | A1. Pending A6. Pending B6. Pending A15. Pending | 4 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1443 | A68FA64E080104E0 |  | Margham | Area 10 | Discharge Gas Cooler Skid | 55.6193569,24.9765665 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | Not Available | Not Available | Vibration switch -10-E-108B-MB | Frank W Murphy | VS-2-EX | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available B6. Earth cable not installed | A6. Fix equipment id A6. Fix circuit id B6. Install earth cable |  | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1443 | Ashik Kasim | 2023-09-13 16:12 | A6. Pending A6. Pending B6. Pending | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1444 | B491A64E080104E0 |  | Margham | Area 10 | Discharge Gas Cooler Skid | 55.6193715,24.9762842 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-E-108C-MB | Not Available | Inlet Vapour Cooler Fan 12 | Not visible | Not Available | Not visible | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | A1. Ex data not available A6. Circuit id not available B6. Earth cable not installed A9. Damaged terminal box A9. Unauthorized modifications(silicon applied on terminal box) | A1. Replace equipment unless proven otherwise A6. Fix circuit id B6. Install earth cable A9. Replace equipment A9. Repair or replace equipment |  | 5 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1444 | Ashik Kasim | 2023-09-13 16:16 | A1. Pending A6. Pending B6. Pending A9. Pending A9. Pending | 5 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1445 | 7391A64E080104E0 |  | Margham | Area 10 | Discharge Gas Cooler Skid | 55.6192262,24.9766077 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | Not Available | Not Available | Vibration switch -10-E-108C-MB | Frank W Murphy | VS-2-EX | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | CD | Not Applicable | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available B6. Earth cable not installed | A6. Fix equipment id A6. Fix circuit id B6. Install earth cable |  | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1445 | Ashik Kasim | 2023-09-13 16:17 | A6. Pending A6. Pending B6. Pending | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1446 | 9C91A64E080104E0 |  | Margham | Area 10 | Discharge Gas Cooler Skid | 55.619224,24.9765653 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-E-108D-MB | Not Available | Inlet Vapour Cooler Fan 13 | Not visible | Not Available | Not visible | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | A1. Ex data not available A6. Circuit id not available B6. Earth cable not installed A9. Unauthorized modifications(silicon applied on terminal box) | A1. Replace equipment unless proven otherwise A6. Fix circuit id B6. Install earth cable A9. Repair or replace equipment |  | 4 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1446 | Ashik Kasim | 2023-09-13 16:24 | A1. Pending A6. Pending B6. Pending A9. Pending | 4 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1447 | 7791A64E080104E0 |  | Margham | Area 10 | Discharge Gas Cooler Skid | 55.6192231,24.976638 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | Not Available | Not Available | Vibration switch -10-E-108D-MB | Frank W Murphy | VS-2-EX | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available B6. Earth cable not installed | A6. Fix equipment id A6. Fix circuit id B6. Install earth cable |  | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1447 | Ashik Kasim | 2023-09-13 16:26 | A6. Pending A6. Pending B6. Pending | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1448 | 8292A64E080104E0 |  | Margham | Area 10 | Discharge Gas Cooler Skid | 55.6193105,24.9765976 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-E-108D-MA | Not Available | Inlet Vapour Cooler Fan 09 | Not visible | Not Available | Not visible | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | A1. Ex data not available A6. Circuit id not available B6. Earth cable not installed | A1. Replace equipment unless proven otherwise A6. Fix circuit id B6. Install earth cable |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1448 | Ashik Kasim | 2023-09-14 08:06 | A1. Pending A6. Pending B6. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1449 | 312BB64C080104E0 |  | Margham | Area 10 | Discharge Gas Cooler Skid | 55.6192231,24.976638 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | Not Available | Not Available | Vibration switch -10-E-108D-MA | Frank W Murphy | VS-2-EX | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available B6. Earth cable not installed A10. Loose adaptors(conduit fittings) A9. Damaged flexible Conduit | A6. Fix equipment id A6. Fix circuit id B6. Install earth cable A10. Tighten adaptors A9. Replace flexible conduit |  | 5 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1449 | Ashik Kasim | 2023-09-14 08:10 | A6. Pending A6. Pending B6. Pending A10. Pending A9. Pending | 5 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable
1450 | 4C91A64E080104E0 |  | Margham | Area 10 | Discharge Gas Cooler Skid | 55.6192723,24.9765192 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-E-108C-MA | Not Available | Inlet Vapour Cooler Fan 08 | Not visible | Not Available | Not visible | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | A1. Ex data not available A6. Circuit id not available B6. Earth cable not installed | A1. Replace equipment unless proven otherwise A6. Fix circuit id B6. Install earth cable |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1450 | Ashik Kasim | 2023-09-14 08:14 | A1. Pending A6. Pending B6. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1451 | 2192A64E080104E0 |  | Margham | Area 10 | Discharge Gas Cooler Skid | 55.6191954,24.976489 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | Not Available | Not Available | Vibration switch -10-E-108C-MA | Frank W Murphy | VS-2-EX | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available B6. Earth cable not installed A10. Loose adaptors(conduit fittings) | A6. Fix equipment id A6. Fix circuit id B6. Install earth cable A10. Tighten adaptors |  | 4 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1451 | Ashik Kasim | 2023-09-14 08:16 | A6. Pending A6. Pending B6. Pending A10. Pending | 4 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1452 | AC91A64E080104E0 |  | Margham | Area 10 | Discharge Gas Cooler Skid | 55.6191762,24.9764442 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-E-108B-MA | Not Available | Inlet Vapour Cooler Fan 07 | Not visible | Not Available | Not visible | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | A1. Ex data not available A6. Circuit id not available B6. Earth cable not installed | A1. Replace equipment unless proven otherwise A6. Fix circuit id B6. Install earth cable |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1452 | Ashik Kasim | 2023-09-14 08:20 | A1. Pending A6. Pending B6. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1453 | 9729B64C080104E0 |  | Margham | Area 10 | Discharge Gas Cooler Skid | 55.6190722,24.9764667 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | Not Available | Not Available | Vibration switch -10-E-108B-MA | Frank W Murphy | VS-2-EX | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available B6. Earth cable not installed | A6. Fix equipment id A6. Fix circuit id B6. Install earth cable |  | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1453 | Ashik Kasim | 2023-09-14 08:23 | A6. Pending A6. Pending B6. Pending | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1454 | A72AB64C080104E0 |  | Margham | Area 10 | Discharge Gas Cooler Skid | 55.6191493,24.9763531 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-E-108A-MA | Not Available | Inlet Vapour Cooler Fan 06 | Not visible | Not Available | Not visible | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | A1. Ex data not available A6. Circuit id not available B6. Earth cable not installed | A1. Replace equipment unless proven otherwise A6. Fix circuit id B6. Install earth cable |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1454 | Ashik Kasim | 2023-09-14 08:26 | A1. Pending A6. Pending B6. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1455 | B829B64C080104E0 |  | Margham | Area 10 | Discharge Gas Cooler Skid | 55.6191302,24.9763457 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | Not Available | Not Available | Vibration switch -10-E-108A-MA | Frank W Murphy | VS-2-EX | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available B6. Earth cable not installed | A6. Fix equipment id A6. Fix circuit id B6. Install earth cable |  | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1455 | Ashik Kasim | 2023-09-14 08:27 | A6. Pending A6. Pending B6. Pending | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1456 | 942BB64C080104E0 |  | Margham | Area 10 | Discharge Gas Cooler Skid | 55.619345,24.9763213 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-E-109A-MB | Not Available | Inlet Liquid Cooler Fan 04 | Spartan Motor | CJB4/5K57110001 | Not visible | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed A15. Flange joint gaps exceeded permitted value A7. Damaged gasket(wrong type used) A1. Ex data not available | A6. Fix circuit id B6. Install earth cable A15. Repair equipment by maintaining the IP A7. Replace with manufacture recommended gasket A1. Replace equipment unless proven otherwise |  | 5 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1456 | Ashik Kasim | 2023-09-14 09:00 | A6. Pending B6. Pending A15. Pending A7. Pending A1. Pending | 5 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1457 | 8F2CB64C080104E0 |  | Margham | Area 10 | Discharge Gas Cooler Skid | 55.619201,24.9763762 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | Not Available | Not Available | Vibration switch -10-E-109A-MB | Frank W Murphy | VS-2-EX | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available B6. Earth cable not installed B3. Trunking, ducts or pipes not sealed properly | A6. Fix equipment id A6. Fix circuit id B6. Install earth cable B3. Apply sealing compound or device |  | 4 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1457 | Ashik Kasim | 2023-09-14 09:03 | A6. Pending A6. Pending B6. Pending B3. Pending | 4 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1458 | E82BB64C080104E0 |  | Margham | Area 10 | Discharge Gas Cooler Skid | 55.6190982,24.976333 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-E-107B-MB | Not Available | Cond Cooler Fan 012 | Spartan Motor | CJB4/5K57110001 | Not visible | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed A7. Damaged gasket(need to verify) A1. Ex data not available | A6. Fix circuit id B6. Install earth cable A7. Replace with manufacture recommended gasket A1. Replace equipment unless proven otherwise |  | 4 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1458 | Ashik Kasim | 2023-09-14 08:59 | A6. Pending B6. Pending A7. Pending A1. Pending | 4 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1459 | 9390A64E080104E0 |  | Margham | Area 10 | Discharge Gas Cooler Skid | 55.6190791,24.9763077 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | Not Available | Not Available | Vibration switch -10-E-107B-MB | Frank W Murphy | VS-2-EX | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available B6. Earth cable not installed B3. Trunking, ducts or pipes not sealed properly | A6. Fix equipment id A6. Fix circuit id B6. Install earth cable B3. Apply sealing compound or device |  | 4 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1459 | Ashik Kasim | 2023-09-14 09:02 | A6. Pending A6. Pending B6. Pending B3. Pending | 4 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1460 | 742BB64C080104E0 |  | Margham | Area 10 | Discharge Gas Cooler Skid | 55.6190977,24.9762813 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-E-107A-MB | Not Available | Cond Cooler Fan 010 | Spartan Motor | CJB4/5K57110001 | Not visible | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed A7. Damaged gasket(need to verify) A1. Ex data not available | A6. Fix circuit id B6. Install earth cable A7. Replace with manufacture recommended gasket A1. Replace equipment unless proven otherwise |  | 4 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1460 | Ashik Kasim | 2023-09-14 09:06 | A6. Pending B6. Pending A7. Pending A1. Pending | 4 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1461 | D52BB64C080104E0 |  | Margham | Area 10 | Discharge Gas Cooler Skid | 55.6191079,24.9762512 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | Not Available | Not Available | Vibration switch -10-E-107A-MB | Frank W Murphy | VS-2-EX | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available B6. Earth cable not installed B3. Trunking, ducts or pipes not sealed properly | A6. Fix equipment id A6. Fix circuit id B6. Install earth cable B3. Apply sealing compound or device |  | 4 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1461 | Ashik Kasim | 2023-09-14 09:08 | A6. Pending A6. Pending B6. Pending B3. Pending | 4 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1462 | 4891A64E080104E0 |  | Margham | Area 10 | Discharge Gas Cooler Skid | 55.6190721,24.9762486 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-E-107A-MB | Not Available | Cond Cooler Fan 09 | Spartan Motor | CJB4/5K57110001 | Not visible | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed A7. Damaged gasket(need to verify) A1. Ex data not available | A6. Fix circuit id B6. Install earth cable A7. Replace with manufacture recommended gasket A1. Replace equipment unless proven otherwise |  | 4 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1462 | Ashik Kasim | 2023-09-14 09:12 | A6. Pending B6. Pending A7. Pending A1. Pending | 4 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1463 | A78FA64E080104E0 |  | Margham | Area 10 | Discharge Gas Cooler Skid | 55.6190341,24.9762051 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | Not Available | Not Available | Vibration switch -10-E-107A-MA | Frank W Murphy | VS-2-EX | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available B6. Earth cable not installed B3. Trunking, ducts or pipes not sealed properly | A6. Fix equipment id A6. Fix circuit id B6. Install earth cable B3. Apply sealing compound or device |  | 4 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1463 | Ashik Kasim | 2023-09-14 09:13 | A6. Pending A6. Pending B6. Pending B3. Pending | 4 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1464 | EB91A64E080104E0 |  | Margham | Area 10 | Discharge Gas Cooler Skid | 55.6190955,24.9762593 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-E-107B-MA | Not Available | Cond Cooler Fan 11 | Spartan Motor | CJB4/5K57110001 | Not visible | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed A7. Damaged gasket(need to verify) A1. Ex data not available | A6. Fix circuit id B6. Install earth cable A7. Replace with manufacture recommended gasket A1. Replace equipment unless proven otherwise |  | 4 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1464 | Ashik Kasim | 2023-09-14 09:17 | A6. Pending B6. Pending A7. Pending A1. Pending | 4 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1465 | C52CB64C080104E0 |  | Margham | Area 10 | Discharge Gas Cooler Skid | 55.6190341,24.9762051 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | Not Available | Not Available | Vibration switch -10-E-107B-MA | Frank W Murphy | VS-2-EX | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available B6. Earth cable not installed B3. Trunking, ducts or pipes not sealed properly | A6. Fix equipment id A6. Fix circuit id B6. Install earth cable B3. Apply sealing compound or device |  | 4 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1465 | Ashik Kasim | 2023-09-14 09:18 | A6. Pending A6. Pending B6. Pending B3. Pending | 4 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1466 | AE29B64C080104E0 |  | Margham | Area 10 | Discharge Gas Cooler Skid | 55.6191023,24.9763366 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-E-109A-MA | Not Available | Inlet Liquid Cooler Fan 03 | Spartan Motor | CJB4/5K57110001 | Not visible | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed A1. Ex data not available | A6. Fix circuit id B6. Install earth cable A1. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1466 | Ashik Kasim | 2023-09-14 09:21 | A6. Pending B6. Pending A1. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1467 | 432BB64C080104E0 |  | Margham | Area 10 | Discharge Gas Cooler Skid | 55.6190909,24.9763419 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | Not Available | Not Available | Vibration switch -10-E-109A-MA | Frank W Murphy | VS-2-EX | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available B6. Earth cable not installed B3. Trunking, ducts or pipes not sealed properly | A6. Fix equipment id A6. Fix circuit id B6. Install earth cable B3. Apply sealing compound or device |  | 4 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1467 | Ashik Kasim | 2023-09-14 09:25 | A6. Pending A6. Pending B6. Pending B3. Pending | 4 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1468 | 9E2AB64C080104E0 |  | Margham | Area 10 | Condensate Handling Area | 55.6187642,24.9764627 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-P-106A | Not Available | Reflux pump motor | Reliance Electrical | Not Available | 01MAF98179 | Electrical | Not Available | Not Available | NEC | Class 1 | D | T3C | Not Available | 60 | CSA | Not Available | Not Applicable | Motor | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed | A6. Fix circuit id B6. Install earth cable |  | 2 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1468 | Ashik Kasim | 2023-09-14 10:16 | A6. Pending B6. Pending | 2 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1469 | AB2AB64C080104E0 |  | Margham | Area 10 | Condensate Handling Area | 55.6187522,24.9764819 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-P-106B | Not Available | Reflux pump motor | Reliance Electrical | Not Available | 01MAF98179 | Electrical | Not Available | Not Available | NEC | Class 1 | D | T3C | Not Available | 60 | CSA | Not Available | Not Applicable | Motor | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed | A6. Fix circuit id B6. Install earth cable |  | 2 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1469 | Ashik Kasim | 2023-09-14 10:23 | A6. Pending B6. Pending | 2 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1470 | CA2BB64C080104E0 |  | Margham | Area 10 | Condensate Handling Area | 55.6187863,24.9764356 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-P-106B | Not Available | LCS- 10-P-106B | Killark | FXCS-OB4U-LO | Not visible | Electrical | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed | A6. Fix circuit id B6. Install earth cable |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1470 | Ashik Kasim | 2023-09-14 10:30 | A6. Pending B6. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1471 | 192DB64C080104E0 |  | Margham | Area 10 | Condensate Handling Area | 55.618732,24.9764673 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-P-106B | Not Available | LCS- 10-P-106B | Killark | FXCS-OB4-LO | 0820 | Electrical | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed | A6. Fix circuit id B6. Install earth cable |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1471 | Ashik Kasim | 2023-09-14 10:31 | A6. Pending B6. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1472 | 7E90A64E080104E0 |  | Margham | Area 10 | Condensate Handling Area | 55.6187381,24.9765386 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-P-206A | 10-P217 | Raw circulate Recirculation pump motor | US Electrical Motor | Not Available | 469776600 | Electrical | Not Available | Not Available | NEC | Class 1 | D | T3 | Not Available | Not Available | Not Available | Not Available | Not Applicable | Motor | Periodic | d | Close | B6. Broken earth connection(Double Earthing required) | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1472 | Ashik Kasim | 2023-09-14 10:50 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1473 | B28FA64E080104E0 |  | Margham | Area 10 | Condensate Handling Area | 55.6187066,24.9765195 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-P-206B | Not Available | Raw circulate Recirculation pump motor | US Electrical Motor | Not Available | 469776600 | Electrical | Not Available | Not Available | NEC | Class 1 | D | T3 | Not Available | Not Available | Not Available | Not Available | Not Applicable | Motor | Periodic | d | Close | B6. Broken earth connection(Double Earthing required) A6. Circuit id not available | B6. Reinstate connection A6. Fix circuit id |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1473 | Ashik Kasim | 2023-09-14 10:56 | B6. Pending A6. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1474 | D42BB64C080104E0 |  | Margham | Area 10 | Condensate Handling Area | 55.6187725,24.9765241 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | MCS-10-P-206B | 10-C225 | LCS-RAW CONDENSATE PUMP | CEAG | Not visible | Not visible | Electrical | 2 | Not Available | IEC | Ex de | IIC | T6 | IP66 | +55 | PTB | PTB99ATEX1044 | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1474 | Ashik Kasim | 2023-09-14 11:01 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1475 | C090A64E080104E0 |  | Margham | Area 10 | Condensate Handling Area | 55.6187737,24.9765507 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | MCS-10-P-206A | 10-C218 | LCS-RAW CONDENSATE PUMP | CEAG | Not visible | Not visible | Electrical | 2 | Not Available | IEC | Ex de | IIC | T6 | IP66 | +55 | PTB | PTB99ATEX1044 | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1475 | Ashik Kasim | 2023-09-14 11:06 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1476 | E32AB64C080104E0 |  | Margham | Area 10 | Condensate Recycle Skid | 55.6190823,24.9762206 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-P-111B | 10-P222 | Condensate Recycle pump motor | Emerson Motor Company | Not Available | YC20P1ZS-P | Electrical | Not Available | Not Available | NEC | Class 1 | D | T3 | Not Available | Not Available | CSA | Not Available | Not Applicable | Motor | Periodic | d | Close | A10. Multiple adaptors/reducers used B6. Earth cable not installed | A10. Replace with single adaptor/reducer B6. Install earth cable |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1476 | Ashik Kasim | 2023-09-14 11:17 | A10. Pending B6. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1477 | 342CB64C080104E0 |  | Margham | Area 10 | Condensate Recycle Skid | 55.619081,24.9762294 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | 10-P-111A | 10-P215 | Condensate Recycle pump motor | Emerson Motor Company | Not Available | YC20P1ZS-P | Electrical | Not Available | Not Available | NEC | Class 1 | D | T3 | Not Available | Not Available | CSA | Not Available | Not Applicable | Motor | Periodic | d | Close | A10. Multiple adaptors/reducers used B6. Earth cable not installed | A10. Replace with single adaptor/reducer B6. Install earth cable |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1477 | Ashik Kasim | 2023-09-14 11:19 | A10. Pending B6. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1478 | 5529B64C080104E0 |  | Margham | Area 10 | Condensate Recycle Skid | 55.6190327,24.9762005 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | MCS-10-P-111A | Not Available | LCS-10-P-111A | CEAG | GHG 434 0004 L9001 | Not Available | Electrical | 2 | Not Available | IEC | Ex de | IIC | T6 | IP66 | -55 +55 | PTB | IECEx BKI 04.0003 | Not Applicable | Others | Periodic | d | Close | B6. Broken earth connection A9. Damaged equipment A15. Flange joint gaps exceeded permitted value | B6. Reinstate connection A9. Replace equipment A15. Repair equipment by maintaining the IP |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1478 | Ashik Kasim | 2023-09-14 11:29 | B6. Pending A9. Pending A15. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable
1479 | BF2BB64C080104E0 |  | Margham | Area 10 | Condensate Recycle Skid | 55.6190445,24.9762003 | Zone 2 | IIB | T3 | IP54 | 4704-EE-10-A0-001-01 |  | MCS-10-P-111B | Not Available | LCS-10-P-111B | CEAG | GHG 434 0004 L9001 | Not Available | Electrical | 2 | Not Available | IEC | Ex de | IIC | T6 | IP66 | -55 +55 | PTB | IECEx BKI 04.0003 | Not Applicable | Others | Periodic | d | Close | B6. Broken earth connection A15. Flange joint gaps exceeded permitted value(need to verify) | B6. Reinstate connection A15. Repair equipment by maintaining the IP |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1479 | Ashik Kasim | 2023-09-14 11:38 | B6. Pending A15. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1480 | 4B2CB64C080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-101(+25 Deck) | 55.6176059,24.9765522 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-E-101D-MA | 95-P-363 | Discharge Gas Cooler D | Reliance Electric | Not Available | 7486506-001 | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | CD | T3 | Not Available | +65 | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Broken earth connection(double earthing required) | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1480 | Ashik Kasim | 2023-09-15 08:44 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1481 | 8E92A64E080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-101(+25 Deck) | 55.6176723,24.9765543 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-XSSH-9525D | 95-XSSH-9525D | Vibration switch | Frank W Murphy | VS-2-EX | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1481 | Ashik Kasim | 2023-09-15 09:03 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1482 | 692CB64C080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-101(+25 Deck) | 55.6176716,24.9764858 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-E-101D-MB | 95-P-367 | Discharge Gas Cooler D | Reliance Electric | Not Available | 7486506-001 | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | CD | T3 | Not Available | +65 | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Broken earth connection(double earthing required) | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1482 | Ashik Kasim | 2023-09-15 09:05 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1483 | 5A29B64C080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-101(+25 Deck) | 55.6177451,24.9765388 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-XSSH-9525H | 95-XSSH-9525H | Vibration switch | Frank W Murphy | VS-2-EX | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1483 | Ashik Kasim | 2023-09-15 09:12 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1484 | A129B64C080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-101(+25 Deck) | 55.6176579,24.9762781 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-E-101C-MA | 95-P-355 | Discharge Gas Cooler C | Reliance Electric | Not Available | 7486506-001 | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | CD | T3 | Not Available | +65 | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Broken earth connection(double earthing required) | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1484 | Ashik Kasim | 2023-09-15 09:18 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1485 | 8590A64E080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-101(+25 Deck) | 55.6175883,24.9764462 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-XSSH-9525C | 95-XSSH-9525C | Vibration switch | Frank W Murphy | VS-2-EX | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1485 | Ashik Kasim | 2023-09-15 09:22 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1486 | 0E20B74C080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-101(+25 Deck) | 55.6176997,24.9764273 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-E-101C-MB | 95-P-359 | Discharge Gas Cooler C | Reliance Electric | Not Available | 7486506-001 | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | CD | T3 | Not Available | +65 | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Broken earth connection(double earthing required) | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1486 | Ashik Kasim | 2023-09-15 09:29 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1487 | B72AB64C080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-101(+25 Deck) | 55.6177254,24.9764568 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-XSSH-9525G | 95-XSSH-9525G | Vibration switch | Frank W Murphy | VS-2-EX | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1487 | Ashik Kasim | 2023-09-15 09:34 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1488 | 442BB64C080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-101(+25 Deck) | 55.6176823,24.9764277 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-E-101B-MA | 95-P-347 | Discharge Gas Cooler B | Reliance Electric | Not Available | 7486506-001 | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | CD | T3 | Not Available | +65 | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Broken earth connection(double earthing required) | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1488 | Ashik Kasim | 2023-09-15 10:06 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1489 | F82AB64C080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-101(+25 Deck) | 55.6176209,24.9763982 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-XSSH-9525B | 95-XSSH-9525B | Vibration switch | Frank W Murphy | VS-2-EX | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1489 | Ashik Kasim | 2023-09-15 10:10 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1490 | 0491A64E080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-101(+25 Deck) | 55.6176249,24.9763967 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-E-101B-MB | 95-P-351 | Discharge Gas Cooler B | Reliance Electric | Not Available | 7486506-001 | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | CD | T3 | Not Available | +65 | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Broken earth connection(double earthing required) | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1490 | Ashik Kasim | 2023-09-15 10:13 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1491 | 3E91A64E080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-101(+25 Deck) | 55.6177158,24.9763997 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-XSSH-9525F | 95-XSSH-9525F | Vibration switch | Frank W Murphy | VS-2-EX | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1491 | Ashik Kasim | 2023-09-15 10:15 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1492 | E691A64E080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-101(+25 Deck) | 55.6176561,24.9763597 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-E-101A-MA | 95-P-339 | Discharge Gas Cooler A | Reliance Electric | Not Available | 7486506-001 | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | CD | T3 | Not Available | +65 | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Broken earth connection(double earthing required) | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1492 | Ashik Kasim | 2023-09-15 10:21 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1493 | E58FA64E080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-101(+25 Deck) | 55.6176213,24.9763205 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-XSSH-9525A | 95-XSSH-9525A | Vibration switch | Frank W Murphy | VS-2-EX | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1493 | Ashik Kasim | 2023-09-15 10:23 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1494 | 152CB64C080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-101(+25 Deck) | 55.6176947,24.9763653 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-E-101A-MB | 95-P-343 | Discharge Gas Cooler A | Reliance Electric | Not Available | 7486506-001 | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | CD | T3 | Not Available | +65 | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Broken earth connection(double earthing required) | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1494 | Ashik Kasim | 2023-09-15 10:27 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1495 | A291A64E080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-101(+25 Deck) | 55.6177225,24.9763073 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-XSSH-9525E | 95-XSSH-9525E | Vibration switch | Frank W Murphy | VS-2-EX | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1495 | Ashik Kasim | 2023-09-15 10:32 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1496 | 8B92A64E080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-201(+25 Deck) | 55.6171,24.9764968 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-E-201D-MA | 95-P-463 | Discharge Gas Cooler D | Reliance Electric | Not Available | 7486506-001 | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | CD | T3 | Not Available | +65 | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Broken earth connection(double earthing required) | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1496 | Ashik Kasim | 2023-09-15 11:05 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1497 | EE2BB64C080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-201(+25 Deck) | 55.617085,24.9765488 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-XSSH-9575D | 95-XSSH-9575D | Vibration switch | Frank W Murphy | VS-2-EX | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1497 | Ashik Kasim | 2023-09-15 11:07 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1498 | 1091A64E080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-201(+25 Deck) | 55.6171715,24.9765283 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-E-201D-MB | 95-P-467 | Discharge Gas Cooler D | Reliance Electric | Not Available | 7486506-001 | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | CD | T3 | Not Available | +65 | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Broken earth connection(double earthing required) | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1498 | Ashik Kasim | 2023-09-15 11:12 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1499 | EA2CB64C080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-201(+25 Deck) | 55.6171547,24.9765546 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-XSSH-9575H | 95-XSSH-9575H | Vibration switch | Frank W Murphy | VS-2-EX | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1499 | Ashik Kasim | 2023-09-15 11:13 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1500 | D82AB64C080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-201(+25 Deck) | 55.6171149,24.976459 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-E-201C-MA | 95-P-455 | Discharge Gas Cooler C | Reliance Electric | Not Available | 7486506-001 | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | CD | T3 | Not Available | +65 | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Broken earth connection(double earthing required) | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1500 | Ashik Kasim | 2023-09-15 11:17 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1501 | 9D2CB64C080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-201(+25 Deck) | 55.6170585,24.9764476 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-XSSH-9575C | 95-XSSH-9575C | Vibration switch | Frank W Murphy | VS-2-EX | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1501 | Ashik Kasim | 2023-09-15 11:19 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1502 | FE91A64E080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-201(+25 Deck) | 55.6171163,24.9764717 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-E-201C-MB | 95-P-459 | Discharge Gas Cooler C | Reliance Electric | Not Available | 7486506-001 | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | CD | T3 | Not Available | +65 | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Broken earth connection(double earthing required) | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1502 | Ashik Kasim | 2023-09-15 11:21 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1503 | DD2BB64C080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-201(+25 Deck) | 55.6171242,24.9764507 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-XSSH-9575G | 95-XSSH-9575G | Vibration switch | Frank W Murphy | VS-2-EX | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1503 | Ashik Kasim | 2023-09-15 11:22 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1504 | 6891A64E080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-201(+25 Deck) | 55.6170009,24.9763937 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-E-201B-MA | 95-P-447 | Discharge Gas Cooler B | Reliance Electric | Not Available | 7486506-001 | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | CD | T3 | Not Available | +65 | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Broken earth connection(double earthing required) | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1504 | Ashik Kasim | 2023-09-15 11:27 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1505 | 5F2BB64C080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-201(+25 Deck) | 55.6169508,24.9763627 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-XSSH-9575B | 95-XSSH-9575B | Vibration switch | Frank W Murphy | VS-2-EX | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1505 | Ashik Kasim | 2023-09-15 11:28 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1506 | F429B64C080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-201(+25 Deck) | 55.6172237,24.9763621 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-E-201B-MB | 95-P-451 | Discharge Gas Cooler B | Reliance Electric | Not Available | 7486506-001 | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | CD | T3 | Not Available | +65 | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Broken earth connection(double earthing required) | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1506 | Ashik Kasim | 2023-09-15 11:31 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1507 | E02CB64C080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-201(+25 Deck) | 55.6172116,24.9764166 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-XSSH-9575F | 95-XSSH-9575F | Vibration switch | Frank W Murphy | VS-2-EX | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1507 | Ashik Kasim | 2023-09-15 11:34 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1508 | E591A64E080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-201(+25 Deck) | 55.6168597,24.9762207 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-E-201A-MA | 95-P-439 | Discharge Gas Cooler A | Reliance Electric | Not Available | 7486506-001 | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | CD | T3 | Not Available | +65 | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Broken earth connection(double earthing required) | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1508 | Ashik Kasim | 2023-09-15 11:45 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1509 | CE2AB64C080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-201(+25 Deck) | 55.617053,24.9763092 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-XSSH-9575A | 95-XSSH-9575A | Vibration switch | Frank W Murphy | VS-2-EX | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1509 | Ashik Kasim | 2023-09-15 11:46 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1510 | 4792A64E080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-201(+25 Deck) | 55.6171127,24.9763559 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-E-201A-MB | 95-P-443 | Discharge Gas Cooler A | Reliance Electric | Not Available | 7486506-001 | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | CD | T3 | Not Available | +65 | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Broken earth connection(double earthing required) | B6. Reinstate connection |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1510 | Ashik Kasim | 2023-09-15 11:49 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1511 | 3890A64E080104E0 |  | Margham | Area 95 | Discharge Cooler Fan Area 95-E-201(+25 Deck) | 55.6172365,24.9763316 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-XSSH-9575E | 95-XSSH-9575E | Vibration switch | Frank W Murphy | VS-2-EX | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1511 | Ashik Kasim | 2023-09-15 11:52 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1512 | 4A92A64E080104E0 |  | Margham | Area 95 | 95-E-101(Top +45)Near Scrubber Area | 55.6176551,24.9765355 | Zone 2 | IIB | T3 | IP65 | EE95-A1-600-01 |  | 95-ZS0-9594 | Not Available | POSITION SWITCH- Suction Scrubber -9594 | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close | B6. Earth cable not installed A6. Circuit id not available | B6. Install earth cable A6. Fix circuit id |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1512 | Ashik Kasim | 2023-09-18 08:34 | B6. Pending A6. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1513 | 02C2AB4E080104E0 |  | Margham | Area 95 | 95-E-101(Top +45)Near Scrubber Area | 55.6176477,24.9765543 | Zone 2 | IIB | T3 | IP65 | EE95-A1-600-01 |  | 95-XV-9540 | 95-XSV-9540 | Junction Box- Suction Scrubber -9540 | Not Available | Not Available | Not visible | Instrumentation | Not Available | Not Available | IEC | Not Available | Not Available | T5 | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed A1. Non conformant equipment | B6. Install earth cable A1. Replace equipment unless proven otherwise |  | 2 |  | Red | 1 | Major Repair Required | Not Applicable | Not Applicable |  | Data Sheet 1513 | Ashik Kasim | 2023-09-18 08:39 | B6. Pending A1. Pending | 2 |  | Red | 1 | Major Repair Required | Not Applicable | Not Applicable
1514 | 792AB64C080104E0 |  | Margham | Area 95 | 95-E-101(Top +30)Near Scrubber Area | 55.6175711,24.9765266 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 319 | 95L-JB319--ST33-33 | Junction Box | Hoffman | Not Available | Not Available | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | e | Close | A6. Equipment id not available A1. Non certified equipment | A6. Fix equipment id A1. Replace equipment |  | 2 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1514 | Ashik Kasim | 2023-09-18 08:45 | A6. Pending A1. Pending | 2 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable
1515 | 6A8FA64E080104E0 |  | Margham | Area 95 | 95-E-101(Top +30)Near Scrubber Area | 55.617581,24.9765379 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 318 | 95L-JB318--ST44-44 | Junction Box | Hoffman | Not Available | Not Available | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | e | Close | A6. Equipment id not available A1. Non certified equipment | A6. Fix equipment id A1. Replace equipment |  | 2 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1515 | Ashik Kasim | 2023-09-18 08:49 | A6. Pending A1. Pending | 2 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable
1516 | D28FA64E080104E0 |  | Margham | Area 95 | 95-E-101(Top +30)Near Scrubber Area | 55.6176615,24.9765313 | Zone 2 | IIB | T3 | IP65 | EE95-A1-600-01 |  | 95-PIT-9504 | 95-PIT-9504 | Pressure Transmitter | Rosemount | 3051S2TG3A3ATTA1JB4D1E5M504015 | 8496098 | Instrumentation | Not Available | Not Available | NEC | CLASS 1 DIV 1 | BCD | T5 | Not Available | -50-+85 | FM | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed A10. Non certified blanking elements installed(need to verify) A10. Loose blanking elements | B6. Install earth cable A10. Replace with suitable type blanking elements A10. Tighten blanking elements |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1516 | Ashik Kasim | 2023-09-18 08:58 | B6. Pending A10. Pending A10. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable
1517 | F72BB64C080104E0 |  | Margham | Area 95 | 95-E-101(Top +30)Near Scrubber Area | 55.6176597,24.9765295 | Zone 2 | IIB | T3 | IP65 | EE95-A1-600-01 |  | 95-PDIT-9502 | 95-PDIT-2502 | Pressure Differential Transmitter | Rosemount | 3051S2TG3A3ATTA1JB4D1E5M504015 | 8496112 | Instrumentation | Not Available | Not Available | NEC | CLASS 1 DIV 1 | BCD | T5 | Not Available | -50-+85 | FM | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed A10. Non certified blanking elements installed A10. Wrong type blanking elements installed(loose and only two threads engaged) | B6. Install earth cable A10. Replace with suitable type blanking elements A10. Replace with suitable type blanking elements |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1517 | Ashik Kasim | 2023-09-18 09:02 | B6. Pending A10. Pending A10. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable
1518 | 618DA64E080104E0 |  | Margham | Area 95 | 95-E-101(Top +30)Near Scrubber Area | 55.6174643,24.9766304 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-AE/TS-9509 | Not Available | IR Flame Detector | Dettronics | X3301A | 19MAY015753 | Instrumentation | 2 | Not Available | IEC | Ex d | IIC | T6 | IP66/67 | -55 +60 | DEMKO | DEMKO02ATEX132195 | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed | A6. Fix circuit id B6. Install earth cable |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1518 | Ashik Kasim | 2023-09-18 09:11 | A6. Pending B6. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1519 | 588FA64E080104E0 |  | Margham | Area 95 | 95-E-101(Top +30)Near Scrubber Area | 55.6175057,24.9765966 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-HS-9509 | Not Available | Flame Detector --Switch | Not visible | ED2SC175-UD1-PBGR-UCLP-RESET-A | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 Div 2 | BCD | T6 | IP56 | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed | A6. Fix circuit id B6. Install earth cable |  | 2 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 1519 | Ashik Kasim | 2023-09-18 09:16 | A6. Pending B6. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable
1520 | FF2AB64C080104E0 |  | Margham | Area 95 | 95-E-101(Top +30)Near Scrubber Area | 55.6176908,24.9766109 | Zone 2 | IIB | T3 | IP65 | EE95-A1-600-01 |  | 95-XV-9501 | 95-XSV-9501A | Junction Box- Suction Scrubber -9501 | Not Available | Not Available | Not visible | Instrumentation | Not Available | Not Available | IEC | Not Available | Not Available | T5 | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed A1. Non conformant equipment | B6. Install earth cable A1. Replace equipment unless proven otherwise |  | 2 |  | Red | 1 | Major Repair Required | Not Applicable | Not Applicable |  | Data Sheet 1520 | Ashik Kasim | 2023-09-18 09:24 | B6. Pending A1. Pending | 2 |  | Red | 1 | Major Repair Required | Not Applicable | Not Applicable
1521 | C32CB64C080104E0 |  | Margham | Area 95 | 95-E-101(Top +30)Near Scrubber Area | 55.6176914,24.9766127 | Zone 2 | IIB | T3 | IP65 | EE95-A1-600-01 |  | 95-ZS0-9501 | 95-ZSO-9501 | POSITION SWITCH- Suction Scrubber -9501 | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close | B6. Earth cable not installed A6. Equipment id not available | B6. Install earth cable A6. Fix equipment id |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1521 | Ashik Kasim | 2023-09-18 09:28 | B6. Pending A6. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1522 | 3A90A64E080104E0 |  | Margham | Area 95 | 95-E-101(Top +30)Near Scrubber Area | 55.6176767,24.9766066 | Zone 2 | IIB | T3 | IP65 | EE95-A1-600-01 |  | 95-XV-9500 | 95-XSV-9500A | Junction Box- Suction Scrubber -9500 | Not Available | Not Available | Not visible | Instrumentation | Not Available | Not Available | IEC | Not Available | Not Available | T5 | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed A1. Non conformant equipment A22. Damaged breathing and draining devices(open entry) | B6. Install earth cable A1. Replace equipment unless proven otherwise A22. Replace with manufacture recommended breathing and draining devices |  | 3 |  | Red | 1 | Major Repair Required | Not Applicable | Not Applicable |  | Data Sheet 1522 | Ashik Kasim | 2023-09-18 09:35 | B6. Pending A1. Pending A22. Pending | 3 |  | Red | 1 | Major Repair Required | Not Applicable | Not Applicable
1523 | 8E90A64E080104E0 |  | Margham | Area 95 | 95-E-101(Top +30)Near Scrubber Area | 55.6176773,24.9766059 | Zone 2 | IIB | T3 | IP65 | EE95-A1-600-01 |  | 95-ZS0-9500 | 95-ZSO-9500 | POSITION SWITCH- Suction Scrubber -9500 | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close | B6. Earth cable not installed A6. Equipment id not available | B6. Install earth cable A6. Fix equipment id |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1523 | Ashik Kasim | 2023-09-18 09:39 | B6. Pending A6. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1524 | 9E90A64E080104E0 |  | Margham | Area 95 | 95-E-101(Top +30)Near Scrubber Area | 55.6175724,24.9765758 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-ZSO-9595/95-ZSC-9595 | 95-ZSO-9595 | Position switch | WESTLOCK | Not Available | Not visible | Instrumentation | Not Available | Not Available | NEC | Class 1 | BCD | Not available | Not Available | Not Available | CSA | Not visible | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed A11. Loose cover | B6. Install earth cable A11. Tighten the cover |  | 2 |  | Yellow | 4 | Minor Repair Required | Normal Operations | Not Applicable |  | Data Sheet 1524 | Ashik Kasim | 2023-09-18 09:49 | B6. Pending A11. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Normal Operations | Not Applicable
1525 | 9129B64C080104E0 |  | Margham | Area 95 | 95-E-101(Top +30)Near Scrubber Area | 55.6175468,24.9765386 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-XSV-9595B | 95-XSV-9595B | Solenoid Valve - Booster Compressor Fast Stop Valve | ASCO Red Hat | Not visible | Not visible | Electrical | Not Available | Not Available | NEC | Class 1 Div 1 | ABCD | Not available | Not Available | Not visible | CSA | Not Available | Not Applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1525 | Ashik Kasim | 2023-09-18 09:52 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1526 | 5790A64E080104E0 |  | Margham | Area 95 | 95-E-101(Top +30)Near Scrubber Area | 55.617554,24.9765379 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-XSV-9595A | 95-XSV-9595A | Solenoid Valve - Booster Compressor Fast Stop Valve | ASCO Red Hat | Not visible | Not visible | Electrical | Not Available | Not Available | NEC | Class 1 Div 1 | ABCD | Not available | Not Available | Not visible | CSA | Not Available | Not Applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1526 | Ashik Kasim | 2023-09-18 09:56 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1527 | 4791A64E080104E0 |  | Margham | Area 95 | 95-E-101(Top +30)Near Scrubber Area | 55.6175911,24.9765646 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-XSV-95001B | 95-XSV-95001B | Solenoid Valve - Scrubber Spil Back | ASCO Red Hat | Not visible | Not visible | Electrical | Not Available | Not Available | NEC | Class 1 Div 1 | ABCD | Not available | Not Available | Not visible | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1527 | Ashik Kasim | 2023-09-18 10:06 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1528 | B52AB64C080104E0 |  | Margham | Area 95 | 95-E-101(Top +30)Near Scrubber Area | 55.6176198,24.9765066 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-XSV-95001A | 95-XSV-95001A | Solenoid Valve - Scrubber Spil Back | ASCO Red Hat | Not visible | Not visible | Electrical | Not Available | Not Available | NEC | Class 1 Div 1 | ABCD | Not available | Not Available | Not visible | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed A6. Circuit id not available | B6. Install earth cable A6. Fix circuit id |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1528 | Ashik Kasim | 2023-09-18 10:09 | B6. Pending A6. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1529 | B629B64C080104E0 |  | Margham | Area 95 | 95-E-101(Top +30)Near Scrubber Area | 55.6176079,24.9765376 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-FY-9500 | 95-FY-9500 | Positioner- Booster Compressor -Suction Header valve | Masoneilan | SVI-II | Not visible | Instrumentation | Not Available | Not Available | NEC | Not visible | Not visible | Not available | IP66 | -50+85 | Not visible | Not visible | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed A6. Circuit id not available A10. Wrong type glands installed(Teflon used with gland) | B6. Install earth cable A6. Fix circuit id A10. Replace with suitable type glands/ Remove teflon |  | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1529 | Ashik Kasim | 2023-09-18 10:17 | B6. Pending A6. Pending A10. Pending | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1530 | 8E29B64C080104E0 |  | Margham | Area 95 | 95-E-101(Top +20)Near 95-HV-9703 | 55.6177672,24.9766114 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | Not Available | Solenoid Valve near ZSC-4006 | Bifold fluid power | FP-77U9 | DSA1010-0268 | Instrumentation | 2 | Not Available | IEC | Ex d | IIC | T6 | IP66 | -60 +40 | BAS | BAS02ATEX2048 | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available A3. Ambient temperature not suitable | A6. Fix equipment id A6. Fix circuit id A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Not Applicable | Not Applicable |  | Data Sheet 1530 | Ashik Kasim | 2023-09-18 10:29 | A6. Pending A6. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Not Applicable | Not Applicable
1531 | 61BEAB4E080104E0 |  | Margham | Area 95 | 95-E-101(Top +20)Near 95-HV-9703 | 55.6176801,24.9765799 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | ZSC-4006 | Not Available | Limit switch | Go Switch | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T6 | IP66/68 | -40 +60 | Baseefa | Baseefa 12ATEX0160X | Yes | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed | A6. Fix circuit id B6. Install earth cable |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1531 | Ashik Kasim | 2023-09-18 10:39 | A6. Pending B6. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1532 | D8C1AB4E080104E0 |  | Margham | Area 95 | 95-E-101(Top +20)Near 95-HV-9703 | 55.6176828,24.9766102 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | ZSO-4006 | Not Available | Limit switch | Go Switch | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db eb | IIC | T6 | IP66/68 | -40 +60 | Baseefa | Baseefa 12ATEX0160X | Yes | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed | A6. Fix circuit id B6. Install earth cable |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1532 | Ashik Kasim | 2023-09-18 10:42 | A6. Pending B6. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1533 | E990A64E080104E0 |  | Margham | Area 95 | 95-E-101(Top +25)Near Scrubber Area | 55.6176424,24.9765354 | Zone 2 | IIB | T3 | IP65 | EE95-A1-600-01 |  | 95-PIT-9500 | 95-PIT-9500 | Pressure Transmitter | Rosemount | 3051S2TG3A3ATTA1JB4D1E5M504015 | 8496104 | Instrumentation | Not Available | Not Available | NEC | CLASS 1 DIV 1 | BCD | T5 | Not Available | -50-+85 | FM | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed A10. Non certified blanking elements installed(need to verify) | B6. Install earth cable A10. Replace with suitable type blanking elements |  | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1533 | Ashik Kasim | 2023-09-18 10:53 | B6. Pending A10. Pending | 2 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable
1534 | 4C90A64E080104E0 |  | Margham | Area 95 | 95-E-101(Top +25)Near Scrubber Area | 55.6176732,24.9766104 | Zone 2 | IIB | T3 | IP65 | EE95-A1-600-01 |  | 95-XV-9541 | 95-XSV-9541A | Junction Box- Suction Scrubber -9541 | Not Available | Not Available | Not visible | Instrumentation | Not Available | Not Available | IEC | Not Available | Not Available | T5 | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed A1. Non conformant equipment A10. Weather seal damaged | B6. Install earth cable A1. Replace equipment unless proven otherwise A10. Replace with suitable type glands |  | 3 |  | Red | 1 | Major Repair Required | Not Applicable | Not Applicable |  | Data Sheet 1534 | Ashik Kasim | 2023-09-18 11:03 | B6. Pending A1. Pending A10. Pending | 3 |  | Red | 1 | Major Repair Required | Not Applicable | Not Applicable
1535 | 3F91A64E080104E0 |  | Margham | Area 95 | 95-E-101(Top +25)Near Scrubber Area | 55.61765,24.9766358 | Zone 2 | IIB | T3 | IP65 | EE95-A1-600-01 |  | 95-ZS0-9541 | 95-ZSO-9541 | POSITION SWITCH- Suction Scrubber -9541 | Topworx | Not visible | Not visible | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | IP66/67 | -55 +50 | Sira | Sira04ATEX1218X | Yes | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1535 | Ashik Kasim | 2023-09-18 11:05 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1536 | 6090A64E080104E0 |  | Margham | Area 95 | 95-E-101(Top +30)Near Scrubber Area | 55.61761,24.9765721 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB320-ST-041-041 | Junction Box | Hoffman | Not Available | Not Available | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | e | Close | A6. Equipment id not available A1. Non certified equipment | A6. Fix equipment id A1. Replace equipment |  | 2 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1536 | Ashik Kasim | 2023-09-18 11:11 | A6. Pending A1. Pending | 2 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable
1537 | FB29B64C080104E0 |  | Margham | Area 95 | 95-E-101(Top +30)Near Gas Cooler Fan Area | 55.6176021,24.9765133 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-AE/TS-9508 | Not Available | Flame Detector --Switch | Not visible | ED2SC175-UD1-PBGR-UCLP-RESET-A | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 Div 2 | BCD | T6 | IP56 | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed | A6. Fix circuit id B6. Install earth cable |  | 2 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 1537 | Ashik Kasim | 2023-09-18 11:17 | A6. Pending B6. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable
1538 | 2E90A64E080104E0 |  | Margham | Area 95 | 95-E-101(Top +30)Near Gas Cooler Fan Area | 55.6176064,24.9765126 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-AE-9508 | Not Available | IR Flame Detector | Dettronics | X3301A | 19MAY015753 | Instrumentation | Not Available | Not Available | NEC | Class 1 | BCD | T6 | IP66/67 | -40 +60 | FM | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed A6. Equipment id not available A6. Circuit id not available | B6. Install earth cable A6. Fix equipment id A6. Fix circuit id |  | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1538 | Ashik Kasim | 2023-09-18 11:20 | B6. Pending A6. Pending A6. Pending | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1539 | 8A90A64E080104E0 |  | Margham | Area 95 | Discharge Gas Cooler- 95-E-101(Top +30) | 55.6175875,24.9765051 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-TY-9524D | 95-TY-9524D | I/P Converter | Masoneilan Dresser | 7000 | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T3B | Not Available | -40 +85 | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 1539 | Ashik Kasim | 2023-09-18 11:23 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable
1540 | D32AB64C080104E0 |  | Margham | Area 95 | Discharge Gas Cooler- 95-E-101(Top +30) | 55.6176449,24.9764389 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-TY-9524C | 95-TY-9524C | I/P Converter | Masoneilan Dresser | 7000 | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T3B | Not Available | -40 +85 | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 1540 | Ashik Kasim | 2023-09-18 11:24 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable
1541 | A98FA64E080104E0 |  | Margham | Area 95 | Discharge Gas Cooler- 95-E-101(Top +30) | 55.6176296,24.9764106 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-TY-9524B | 95-TY-9524B | I/P Converter | Masoneilan Dresser | 7000 | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T3B | Not Available | -40 +85 | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 1541 | Ashik Kasim | 2023-09-18 11:26 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable
1542 | 8C92A64E080104E0 |  | Margham | Area 95 | Discharge Gas Cooler- 95-E-101(Top +30) | 55.6176205,24.9763914 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-TY-9524A | 95-TY-9524A | I/P Converter | Masoneilan Dresser | 7000 | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T3B | Not Available | -40 +85 | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed A6. Circuit id not available | B6. Install earth cable A6. Fix circuit id |  | 2 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 1542 | Ashik Kasim | 2023-09-18 11:27 | B6. Pending A6. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable
1543 | 7B2AB64C080104E0 |  | Margham | Area 95 | Discharge Gas Cooler- 95-E-101(Top +30) | 55.6176006,24.9764158 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | RP-060 | 95L-JB323-RP060-051 | Power Socket | Appleton | 3XR | ENR21202 | Electrical | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1543 | Ashik Kasim | 2023-09-18 11:34 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1544 | 84C4AB4E080104E0 |  | Margham | Area 95 | Discharge Gas Cooler- 95-E-101(Top +30) | 55.6175875,24.9765051 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-AE-9529 | Not Available | Gas Detection Transmitter | Drager | polytron2IR | Not visible | Instrumentation | Not Available | Not Available | NEC | Class 1 Div 1 | BCD | Not available | Not Available | -65 | UL | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed | A6. Fix circuit id B6. Install earth cable |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1544 | Ashik Kasim | 2023-09-18 11:45 | A6. Pending B6. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1545 | E52BB64C080104E0 |  | Margham | Area 95 | Cable Rack- Booster Compressor -Ground | 55.6173172,24.976527 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB303-P077-068 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1545 | Ashik Kasim | 2023-09-19 09:01 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1546 | D02BB64C080104E0 |  | Margham | Area 95 | Cable Rack- Booster Compressor -Ground | 55.6174047,24.9765605 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB302-P088-079 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1546 | Ashik Kasim | 2023-09-19 09:08 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1547 | 0C2CB64C080104E0 |  | Margham | Area 95 | Cable Rack- Booster Compressor -Ground | 55.6175454,24.9765599 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB302-P087-078 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1547 | Ashik Kasim | 2023-09-19 09:13 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1548 | B690A64E080104E0 |  | Margham | Area 95 | Cable Rack- Booster Compressor -Ground | 55.6175281,24.9764695 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB303-P076-067 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1548 | Ashik Kasim | 2023-09-19 09:17 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1549 | 0D91A64E080104E0 |  | Margham | Area 95 | Cable Rack- Booster Compressor -Ground | 55.6174781,24.9762649 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB302-P086-077 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1549 | Ashik Kasim | 2023-09-19 09:22 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1550 | 958DA64E080104E0 |  | Margham | Area 95 | Cable Rack- Booster Compressor -Ground | 55.6174033,24.9763462 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB302-P085-072 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1550 | Ashik Kasim | 2023-09-19 09:28 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1551 | CE29B64C080104E0 |  | Margham | Area 95 | Cable Rack- Booster Compressor -Ground | 55.6174785,24.9763459 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB303-P075-066 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1551 | Ashik Kasim | 2023-09-19 09:32 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1552 | CB29B64C080104E0 |  | Margham | Area 95 | Cable Rack- Booster Compressor -Ground | 55.6174964,24.9761016 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB302-P084-075 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1552 | Ashik Kasim | 2023-09-19 09:38 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1553 | C191A64E080104E0 |  | Margham | Area 95 | Cable Rack- Booster Compressor -Ground | 55.6173908,24.9761747 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB302-P083-074 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1553 | Ashik Kasim | 2023-09-19 09:42 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1554 | 762BB64C080104E0 |  | Margham | Area 95 | Cable Rack- Booster Compressor -Ground | 55.6174342,24.9761407 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB303-P074-065 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1554 | Ashik Kasim | 2023-09-19 09:46 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1555 | 0FFAA64E080104E0 |  | Margham | Area 95 | Cable Rack- Booster Compressor -Ground | 55.617355,24.976253 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB302-P082-073 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1555 | Ashik Kasim | 2023-09-19 10:01 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1556 | E72CB64C080104E0 |  | Margham | Area 95 | Cable Rack- Booster Compressor -Ground | 55.6175371,24.9760882 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB302-P081-072 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1556 | Ashik Kasim | 2023-09-19 10:06 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1557 | 2592A64E080104E0 |  | Margham | Area 95 | Cable Rack- Booster Compressor -Ground | 55.6174868,24.9759946 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB303-P073-064 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1557 | Ashik Kasim | 2023-09-19 10:10 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1558 | 77CBA64E080104E0 |  | Margham | Area 95 | Cable Rack- Booster Compressor -Ground | 55.6173594,24.9760256 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB302-P080-071 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1558 | Ashik Kasim | 2023-09-19 10:14 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1559 | 4491A64E080104E0 |  | Margham | Area 95 | Cable Rack- Booster Compressor -Ground | 55.6172932,24.9762669 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB303-P073-063 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1559 | Ashik Kasim | 2023-09-19 10:19 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1560 | 6C29B64C080104E0 |  | Margham | Area 95 | Cable Rack- Booster Compressor -Ground | 55.6176073,24.9760694 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB302-P079-070 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1560 | Ashik Kasim | 2023-09-19 10:27 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1561 | AE2CB64C080104E0 |  | Margham | Area 95 | Cable Rack- Booster Compressor -Ground | 55.6175709,24.9758976 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB303-P072-063 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1561 | Ashik Kasim | 2023-09-19 10:32 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1562 | 202DB64C080104E0 |  | Margham | Area 95 | Cable Rack- Booster Compressor -Ground | 55.6176081,24.9758811 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB302-P078-069 | Street Light | Appleton | S-55 | KPB150LGPSR | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | Not Available | T3 | IP66 | 40 | UL | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Equipment id not available A3. Temperature class not suitable A3. Ambient temperature not suitable | A6. Fix equipment id A3. Replace equipment A3. Replace equipment unless proven otherwise |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1562 | Ashik Kasim | 2023-09-19 10:39 | A6. Pending A3. Pending A3. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Scaffolding
1563 | CA2AB64C080104E0 |  | Margham | Area 95 | Cable Rack- Booster Compressor -Ground | 55.6176159,24.9758847 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-LJB-301 | 95L-JB301--FL231-184 | Junction Box | Hoffman | Not Available | Not Available | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | e | Close | A1. Non certified equipment | A1. Replace equipment |  | 1 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1563 | Ashik Kasim | 2023-09-19 10:46 | A1. Pending | 1 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable
1564 | 8C2AB64C080104E0 |  | Margham | Area 95 | Cable Rack- Booster Compressor -Ground | 55.617634,24.9760994 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95HS-9502 | Not Available | Fire Alarm Box | MEDC | BGW-R | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T4A | Not Available | -25 +55 | UL | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available A10. Loose adaptors(conduit Coupling) B6. Earth cable not installed | A6. Fix circuit id A10. Tighten adaptors B6. Install earth cable |  | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1564 | Ashik Kasim | 2023-09-19 10:58 | A6. Pending A10. Pending B6. Pending | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1565 | 1B90A64E080104E0 |  | Margham | Area 95 | Cable Rack- Booster Compressor -Ground | 55.6176376,24.9759928 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB302-P076-069 | Junction Box | Hoffman | Not Available | Not Available | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | e | Close | A1. Non certified equipment A6. Equipment id not available | A1. Replace equipment A6. Fix equipment id |  | 2 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1565 | Ashik Kasim | 2023-09-19 11:01 | A1. Pending A6. Pending | 2 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable
1566 | 082BB64C080104E0 |  | Margham | Area 95 | Cable Rack- Booster Compressor -Ground | 55.6175674,24.9760121 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-JBS-01 | Not Available | Junction Box | Not Available | Not Available | Not Available | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | UL | Not Available | Not Applicable | Others | Periodic | e | Close | A1. Non conformant equipment A6. Circuit id not available A10. Loose bolts(chances for ingress of water and dust) | A1. Replace equipment unless proven otherwise A6. Fix circuit id A10. Tighten bolts(Confirm no ingress of water and dust inside JB) |  | 3 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1566 | Ashik Kasim | 2023-09-19 11:12 | A1. Pending A6. Pending A10. Pending | 3 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable
1567 | 7F2BB64C080104E0 |  | Margham | Area 95 | Cable Rack- Booster Compressor -Ground | 55.6175296,24.9760855 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB303-P071-062 | Junction Box | Hoffman | Not Available | Not Available | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | e | Close | A1. Non certified equipment A6. Equipment id not available | A1. Replace equipment A6. Fix equipment id |  | 2 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1567 | Ashik Kasim | 2023-09-19 11:15 | A1. Pending A6. Pending | 2 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable
1568 | E72BB64C080104E0 |  | Margham | Area 95 | Cable Rack- Booster Compressor -Ground | 55.6173939,24.9761622 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | Not Available | 95L-JB304-RP-092-083 | Junction Box | Hoffman | Not Available | Not Available | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | e | Close | A1. Non certified equipment A6. Equipment id not available | A1. Replace equipment A6. Fix equipment id |  | 2 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1568 | Ashik Kasim | 2023-09-19 11:23 | A1. Pending A6. Pending | 2 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable
1569 | 212CB64C080104E0 |  | Margham | Area 95 | Motor Control Station -95-E-101 | 55.6175454,24.976307 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-E-101A-MA | 95-C-340 | LCS | Not Available | ED2S175J1UCLPLPON102ULCN0AA 4/08 | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | BCD | T6 | Not Available | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1569 | Ashik Kasim | 2023-09-19 11:40 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1570 | 2790A64E080104E0 |  | Margham | Area 95 | Motor Control Station -95-E-101 | 55.6175188,24.9763484 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-E-101B-MA | 95-C-348 | LCS | Not Available | ED2S175J1UCLPLPON102ULCN0AA 4/08 | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | BCD | T6 | Not Available | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1570 | Ashik Kasim | 2023-09-19 11:41 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1571 | 0F2CB64C080104E0 |  | Margham | Area 95 | Motor Control Station -95-E-101 | 55.6175314,24.9764238 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-E-101C-MA | 95-C-356 | LCS | Not Available | ED2S175J1UCLPLPON102ULCN0AA 4/08 | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | BCD | T6 | Not Available | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1571 | Ashik Kasim | 2023-09-19 11:43 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1572 | 7191A64E080104E0 |  | Margham | Area 95 | Motor Control Station -95-E-101 | 55.6175291,24.9764018 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-E-101D-MA | 95-C-364 | LCS | Not Available | ED2S175J1UCLPLPON102ULCN0AA 4/08 | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | BCD | T6 | Not Available | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1572 | Ashik Kasim | 2023-09-19 11:44 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1573 | 0F2BB64C080104E0 |  | Margham | Area 95 | Motor Control Station -95-E-101 | 55.6177744,24.9764375 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-101A-MB | 95-C-344 | LCS | Not Available | ED2S175J1UCLPLPON102ULCN0AA 4/08 | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | BCD | T6 | Not Available | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1573 | Ashik Kasim | 2023-09-19 11:47 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1574 | 2E2BB64C080104E0 |  | Margham | Area 95 | Motor Control Station -95-E-101 | 55.6177336,24.9763609 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-E-101B-MB | 95-C-352 | LCS | Not Available | ED2S175J1UCLPLPON102ULCN0AA 4/08 | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | BCD | T6 | Not Available | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1574 | Ashik Kasim | 2023-09-19 11:48 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1575 | 8E2BB64C080104E0 |  | Margham | Area 95 | Motor Control Station -95-E-101 | 55.6177319,24.9763916 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-E-101C-MB | 95-C-360 | LCS | Not Available | ED2S175J1UCLPLPON102ULCN0AA 4/08 | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | BCD | T6 | Not Available | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1575 | Ashik Kasim | 2023-09-19 11:50 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1576 | BE91A64E080104E0 |  | Margham | Area 95 | Motor Control Station -95-E-101 | 55.6177764,24.9763852 | Zone 2 | IIB | T3 | IP54 | EE95-A1-600-01 |  | 95-E-101D-MB | 95-C-368 | LCS | Not Available | ED2S175J1UCLPLPON102ULCN0AA 4/08 | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | BCD | T6 | Not Available | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1576 | Ashik Kasim | 2023-09-19 11:51 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1577 | 2392A64E080104E0 |  | Margham | Area 25 | 25-TF-101 | 55.6169221,24.9750089 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-WLF-001 | 25-PC-873 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-096 | Electrical | Not Available | Gc | IEC | Ex db | IIC | T6 | IP66 | -40 ,+55 | NEP | IECEx NEP18.0003X | Yes | Lighting | Periodic | d | Close | A10. Loose glands B6. Broken earth connection | A10. Tighten glands B6. Reinstate connection |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1577 | Ashik Kasim | 2023-09-20 08:30 | A10. Done B6. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-09-20 09:01
1578 | 4992A64E080104E0 |  | Margham | Area 25 | 25-TF-101 | 55.616931,24.9750054 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-286 | 25-PC-849 | Light Junction Box | Weidmuller | Klippon POK 161609 | XB-AE-A-040378 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECExIBE13.0004X | Yes | Others | Periodic | e | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1578 | Ashik Kasim | 2023-09-20 08:33 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-09-20 09:02
1579 | 002BB64C080104E0 |  | Margham | Area 25 | 25-TF-101 | 55.6169343,24.9750135 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-WLF-002 | 25-PC-874 | Light Fixture | EATON | NHLL-4-C2-8L-1/6-220 | 64223891-091 | Electrical | Not Available | Gc | IEC | Ex db | IIC | T6 | IP66 | -40 ,+55 | NEP | IECEx NEP18.0003X | Yes | Lighting | Periodic | d | Close | A10. Loose glands B6. Broken earth connection | A10. Tighten glands B6. Reinstate connection |  | 2 |  | Yellow | 4 | Minor Repair Required | Not Applicable | Not Applicable |  | Data Sheet 1579 | Ashik Kasim | 2023-09-20 09:39 | A10. Done B6. Done | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable | Ashik Kasim | 2023-09-20 16:34
1580 | 358EA64E080104E0 |  | Margham | Area 25 | 25-TF-101 | 55.6169441,24.9749654 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-LJB-247 | 25-PC-739 | Light Junction Box | Weidmuller | Klippon POK 161609 | XB-AE-A-040156 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECExIBE13.0004X | Yes | Others | Periodic | e | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1580 | Ashik Kasim | 2023-09-20 08:51 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-09-20 09:26
1581 | 6A29B64C080104E0 |  | Margham | Area 25 | 25-TF-101 | 55.6169038,24.9750179 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-SJB-02 | 25-PC-907 | Light Junction Box | Weidmuller | Klippon POK 161609 | XB-AE-A-040351 | Electrical | Not Available | Gb | IEC | Ex e | IIC | T5 | IP66 | -20 +55 | IBE | IECExIBE13.0004X | Yes | Others | Periodic | e | Close | A10. Loose glands | A10. Tighten glands |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1581 | Ashik Kasim | 2023-09-20 09:01 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-09-20 09:13
1582 | F629B64C080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.6179361,24.9752927 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-GT-121B | 25-GT-121B | GAS DETECTOR TRANSMITTER | MSA | UltimaX5000 | 0001000001280071 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | Not Available | -40 +60 | SIRA | IECEX SIR17.0017X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1582 | Ashik Kasim | 2023-09-20 09:35 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-09-20 09:26
1583 | 392BB64C080104E0 |  | Margham | Area 25 | MEC-Compressor A | 55.617956,24.9753386 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-GT-121A | 25-GT-121A | GAS DETECTOR TRANSMITTER | MSA | UltimaX5000 | 000100000128001A | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | Not Available | -40 +60 | SIRA | IECEX SIR17.0017X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1583 | Ashik Kasim | 2023-09-20 09:45 | A10. Done | 0 |  | Green | Not Applicable | Good to Use | Equipment Isolation | Scaffolding | Ashik Kasim | 2023-09-20 09:13
1584 | 8290A64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar D | 55.6191828,24.9802303 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-BD-10-DR-56 | Not Available | Ex d Enclosure - Roll up Door | ADALET | XJF081006 | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 | BCD | Not available | Not Available | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close | A4. Inappropriate IP protection A6. Equipment id not available A6. Circuit id not available A9. Unauthorized modifications A9. Additional holes drilled B6. Earth cable not installed | A4. Replace equipment A6. Fix equipment id A6. Fix circuit id A9. Repair or replace equipment A9. Replace equipment B6. Install earth cable |  | 6 |  | Red | 1 | Replacement Required | Equipment Isolation | Not Applicable |  | Data Sheet 1584 | Ashik Kasim | 2023-09-20 14:51 | A4. Pending A6. Pending A6. Pending A9. Pending A9. Pending B6. Pending | 6 |  | Red | 1 | Replacement Required | Equipment Isolation | Not Applicable
1585 | DC2AB64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar D | 55.6193007,24.977705 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-BD-10-DR-56 | Not Available | LCS Roll up door 56 | Not Available | Not Available | Not Available | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | A1. Ex data not available A4. Inappropriate IP protection A6. Equipment id not available A6. Circuit id not available B3. Trunking, ducts or pipes not sealed properly B6. Earth cable not installed | A1. Replace equipment unless proven otherwise A4. Replace equipment A6. Fix equipment id A6. Fix circuit id B3. Apply sealing compound or device B6. Install earth cable |  | 6 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1585 | Ashik Kasim | 2023-09-20 15:01 | A1. Pending A4. Pending A6. Pending A6. Pending B3. Pending B6. Pending | 6 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable
1586 | 7591A64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar D | 55.6192644,24.9776947 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-PRI-4 | 30-P470 | Power Socket -480VAC | Crouse Hinds | SRD 3524NW | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 | BCD | Not available | Not Available | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close | A10. Wrong type glands installed(need to verify) A10. Multiple adaptors/reducers used B6. Earth cable not installed | A10. Replace with suitable type glands A10. Replace with single adaptor/reducer B6. Install earth cable |  | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1586 | Ashik Kasim | 2023-09-21 16:33 | A10. Pending A10. Pending B6. Pending | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1587 | C291A64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar D | 55.6191026,24.9777519 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-BD-10-DR-56 | Not Available | Safety limit Sensor Terminal Box- Roll up door 56 | Miller Edge | MT22 Sensing Edge | Not Available | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | A1. Ex data not available A4. Inappropriate IP protection A6. Equipment id not available A6. Circuit id not available B6. Earth cable not installed A11. Loose cover C1. Non-compliance with environmental conditions C2. Accumulation of dust and dirt | A1. Replace equipment unless proven otherwise A4. Replace equipment A6. Fix equipment id A6. Fix circuit id B6. Install earth cable A11. Tighten the cover C1. Relocate or safeguard the equipment C2. Remove the dust and dirt |  | 8 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1587 | Ashik Kasim | 2023-09-20 15:27 | A1. Pending A4. Pending A6. Pending A6. Pending B6. Pending A11. Pending C1. Pending C2. Pending | 8 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable
1588 | 3D29B64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar D | 55.6193008,24.9776894 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-LG 11 | Not Available | Power Socket -240VAC | Course Hinds | CESD2213 | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 | D | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed A10. Multiple adaptors/reducers used | A6. Fix circuit id B6. Install earth cable A10. Replace with single adaptor/reducer |  | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1588 | Ashik Kasim | 2023-09-21 15:47 | A6. Pending B6. Pending A10. Pending | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1589 | 942CB64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar D | 55.6143277,24.9737694 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-GT-001D-01H | Not Available | Ex d Enclosure - Lube Oil Heater | Appleton | GR series | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 | BCD | Not available | Not Available | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available A10. Wrong type glands installed(need to verify) A10. Weather seal damaged B3. Trunking, ducts or pipes not sealed properly | A6. Fix circuit id A10. Replace with suitable type glands A10. Replace with suitable type glands B3. Apply sealing compound or device |  | 4 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1589 | Ashik Kasim | 2023-09-20 15:56 | A6. Pending A10. Pending A10. Pending B3. Pending | 4 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1590 | 2690A64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top | 55.6189987,24.9775907 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-PDT-001D | 30-IC-103 | Pressure Differential Transmitter | Rosemount | 3051S2CD1A2A1W1AE5M5C4 | 8031473 | Instrumentation | Not Available | Not Available | NEC | Class 1 Div 1 | BCD | Not available | Not Available | -50 +85 | FM | Not Available | Not Applicable | Others | Periodic | d | Close | A10. Non certified blanking elements installed(need to verify) A10. Damaged blanking elements( corroded) B6. Earth cable not installed | A10. Replace with suitable type blanking elements A10. Replace with suitable type blanking elements B6. Install earth cable |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1590 | Ashik Kasim | 2023-09-21 09:39 | A10. Pending A10. Pending B6. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable
1591 | 4391A64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top | 55.6189678,24.977616 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | Not Available | 30-C-127 | Ex d Enclosure - Air Filter Control | Killark | EXB-12246 N34 | 12841 | Electrical | Not Available | Not Available | NEC | Class 1 | BCD | Not available | Not Available | Not Available | FM | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available A10. Weather seal damaged B3. Trunking, ducts or pipes not sealed properly | A6. Fix circuit id A10. Replace with suitable type glands B3. Apply sealing compound or device |  | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1591 | Ashik Kasim | 2023-09-21 08:47 | A6. Pending A10. Pending B3. Pending | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1592 | D3F8A64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top | 55.6190615,24.977634 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | Not Available | Not Available | LCS- Air filter -Solar D | Killark | FXCS-0S3C5 | Not Available | Electrical | Not Applicable | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | Not visible | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available A10. Multiple adaptors/reducers used B6. Earth cable not installed B3. Trunking, ducts or pipes not sealed properly | A6. Fix equipment id A6. Fix circuit id A10. Replace with single adaptor/reducer B6. Install earth cable B3. Apply sealing compound or device |  | 5 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1592 | Ashik Kasim | 2023-09-21 11:12 | A6. Pending A6. Pending A10. Pending B6. Pending B3. Pending | 5 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1593 | 8E2CB64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top | 55.6189799,24.9775893 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-FT-0059 | 30-IC-101 | Flow Transmitter | Rosemount | Not visible | 8008439 | Instrumentation | Not Available | Not Available | NEC | Class 1 Div 1 | BCD | Not available | Not Available | Not visible | FM | Not Available | Not Applicable | Others | Periodic | d | Close | A10. Non certified blanking elements installed(need to verify) A10. Damaged blanking elements( corroded) B6. Earth cable not installed | A10. Replace with suitable type blanking elements A10. Replace with suitable type blanking elements B6. Install earth cable |  | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1593 | Ashik Kasim | 2023-09-21 09:37 | A10. Pending A10. Pending B6. Pending | 3 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable
1594 | FB2AB64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top Solar D | 55.6189746,24.9776367 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-GT-001D-EIA | 30-C-454 | LCS- Lube Oil Cooler Fan A | Crouse Hinds | EFSC 228 | Not Available | Electrical | Not Applicable | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | Not visible | Not Available | Not Applicable | Others | Periodic | d | Close | A10. Multiple adaptors/reducers used with stop plug B6. Earth cable not installed | A10. Replace without reducer B6. Install earth cable |  | 2 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1594 | Ashik Kasim | 2023-09-21 09:44 | A10. Pending B6. Pending | 2 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1595 | 022CB64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top Solar D | 55.618999,24.9775835 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-GT-001D-EIA | 30-C-454 | LCS- Lube Oil Cooler Fan B | Crouse Hinds | Not visible | Not Available | Electrical | Not Applicable | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close | A10. Multiple adaptors/reducers used with stop plug B6. Earth cable not installed | A10. Replace without reducer B6. Install earth cable |  | 2 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1595 | Ashik Kasim | 2023-09-21 09:47 | A10. Pending B6. Pending | 2 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1596 | 5D2CB64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top Solar D | 55.6189934,24.977585 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-GT-001D-EIA | 30-C-454 | LCS- Solar D supply Fan | Crouse Hinds | EDS2129 | Not Available | Electrical | Not Applicable | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | Not visible | Not Available | Not Applicable | Others | Periodic | d | Close | A10. Multiple adaptors/reducers used with stop plug B6. Earth cable not installed | A10. Replace without reducer B6. Install earth cable |  | 2 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1596 | Ashik Kasim | 2023-09-21 09:51 | A10. Pending B6. Pending | 2 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1597 | 6290A64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top Solar D | 55.6189434,24.9775027 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | Not Available | Not Available | Receptacle 240vac | FLP | simplex | Not Available | Electrical | Not Available | Not Available | NEC | Not Available | Not available | Not available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | A1. Non conformant equipment A6. Equipment id not available A6. Circuit id not available A9. Unauthorized modifications(equipment painted) B6. Earth cable not installed B3. Trunking, ducts or pipes not sealed properly | A1. Replace equipment unless proven otherwise A6. Fix equipment id A6. Fix circuit id A9. Repair or replace equipment B6. Install earth cable B3. Apply sealing compound or device |  | 6 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1597 | Ashik Kasim | 2023-09-21 10:01 | A1. Pending A6. Pending A6. Pending A9. Pending B6. Pending B3. Pending | 6 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable
1598 | 3491A64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top | 55.6190163,24.9775027 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-FT-0058 | Not Available | Flow Transmitter | Rosemount | Not visible | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 Div 1 | BCD | Not available | Not Available | Not visible | FM | Not Available | Not Applicable | Others | Periodic | d | Close | A10. Non certified blanking elements installed(need to verify) B6. Earth cable not installed A1. Non conformant equipment A6. Circuit id not available | A10. Replace with suitable type blanking elements B6. Install earth cable A1. Replace equipment unless proven otherwise A6. Fix circuit id |  | 4 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1598 | Ashik Kasim | 2023-09-21 10:12 | A10. Pending B6. Pending A1. Pending A6. Pending | 4 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable
1599 | 7991A64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar C | 55.6189409,24.9775363 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | Not Available | Not Available | LCS- Air filter -Solar D | Killark | FXCS-0S3C5 | Not Available | Electrical | Not Applicable | Not Available | NEC | Not Available | Not Available | Not available | Not Available | Not Available | Not visible | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available A10. Multiple adaptors/reducers used B6. Earth cable not installed B3. Trunking, ducts or pipes not sealed properly | A6. Fix equipment id A6. Fix circuit id A10. Replace with single adaptor/reducer B6. Install earth cable B3. Apply sealing compound or device |  | 5 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1599 | Ashik Kasim | 2023-09-21 10:16 | A6. Pending A6. Pending A10. Pending B6. Pending B3. Pending | 5 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1600 | D190A64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top | 55.6189678,24.977616 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | Not Available | Not Available | Ex d Enclosure - Air Filter JB1 | Killark | Not visible | 12841 | Electrical | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | Not visible | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available B3. Trunking, ducts or pipes not sealed properly B6. Earth cable not installed | A6. Fix equipment id A6. Fix circuit id B3. Apply sealing compound or device B6. Install earth cable |  | 4 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1600 | Ashik Kasim | 2023-09-21 10:25 | A6. Pending A6. Pending B3. Pending B6. Pending | 4 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1601 | A52AB64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar C | 55.6189836,24.9775474 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | Not Available | Not Available | Ex d Enclosure - Air Filter JB2 | Killark | Not visible | Not visible | Electrical | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | Not visible | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available B3. Trunking, ducts or pipes not sealed properly B6. Earth cable not installed | A6. Fix equipment id A6. Fix circuit id B3. Apply sealing compound or device B6. Install earth cable |  | 4 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1601 | Ashik Kasim | 2023-09-21 10:31 | A6. Pending A6. Pending B3. Pending B6. Pending | 4 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1602 | B5F9A64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar C | 55.6189613,24.9775332 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | Not Available | Not Available | Pressure Differential Transmitter | Rosemount | 3051CD1A73A1AKDL4M5 | 2260363 | Instrumentation | Not Available | Not Available | IEC | Ex ia | IIC | T4 | IP66 | -60 +70 | BAS | BAS97ATEX1089X | Yes | Others | Periodic | d | Close | A10. Non certified blanking elements installed(need to verify) B6. Earth cable not installed A6. Equipment id not available A6. Circuit id not available | A10. Replace with suitable type blanking elements B6. Install earth cable A6. Fix equipment id A6. Fix circuit id |  | 4 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1602 | Ashik Kasim | 2023-09-21 10:41 | A10. Pending B6. Pending A6. Pending A6. Pending | 4 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable
1603 | 3691A64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar C | 55.6189404,24.9775159 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | Not Available | Not Available | Air filter Solenoid Valve 1 -Solar C | Donaldson company | RCA5V5 | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | D | T4A | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available A10. Bolts missing B6. Earth cable not installed | A6. Fix equipment id A6. Fix circuit id A10. Fix with manufacture recommended bolts B6. Install earth cable |  | 4 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1603 | Ashik Kasim | 2023-09-21 10:54 | A6. Pending A6. Pending A10. Pending B6. Pending | 4 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1604 | CD90A64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar C | 55.6189391,24.9775243 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | Not Available | Not Available | Air filter Solenoid Valve 2 -Solar C | Donaldson company | RCA5V5 | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | D | T4A | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available B6. Earth cable not installed | A6. Fix equipment id A6. Fix circuit id B6. Install earth cable |  | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1604 | Ashik Kasim | 2023-09-21 10:56 | A6. Pending A6. Pending B6. Pending | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1605 | 6F93A64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar C | 55.6189583,24.9775051 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | Not Available | Not Available | Air filter Solenoid Valve 3 -Solar C | Donaldson company | RCA5V5 | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | D | T4A | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available B6. Earth cable not installed | A6. Fix equipment id A6. Fix circuit id B6. Install earth cable |  | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1605 | Ashik Kasim | 2023-09-21 10:57 | A6. Pending A6. Pending B6. Pending | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1606 | 9D2AB64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar C | 55.6189299,24.9774852 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | Not Available | Not Available | Air filter Solenoid Valve 4 -Solar C | Donaldson company | RCA5V5 | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | D | T4A | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available B6. Earth cable not installed | A6. Fix equipment id A6. Fix circuit id B6. Install earth cable |  | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1606 | Ashik Kasim | 2023-09-21 10:58 | A6. Pending A6. Pending B6. Pending | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1607 | DA2AB64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top | 55.6189918,24.9774844 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-GT-001C-EIBM | Not Available | LCS- Cooler Fan Lube Oil-Solar C | Killark | FXCS-0S3C5 | Not Available | Electrical | Not Applicable | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed B3. Trunking, ducts or pipes not sealed properly | A6. Fix circuit id B6. Install earth cable B3. Apply sealing compound or device |  | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1607 | Ashik Kasim | 2023-09-21 11:11 | A6. Pending B6. Pending B3. Pending | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1608 | D429B64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top | 55.6190122,24.9775536 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-GT-001C- EIAM | Not Available | LCS- Cooler Fan Lube Oil-Solar C | Killark | FXCS-0S3C5 | Not Available | Electrical | Not Applicable | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed B3. Trunking, ducts or pipes not sealed properly | A6. Fix circuit id B6. Install earth cable B3. Apply sealing compound or device |  | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1608 | Ashik Kasim | 2023-09-21 11:13 | A6. Pending B6. Pending B3. Pending | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1609 | DE29B64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar D Air Filter | 55.6190726,24.977695 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | Not Available | Not Available | Solenoid Valve -3 Solar Air Filter | GOYEN | RCA3-6V | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | D | T4 | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available B6. Earth cable not installed | A6. Fix equipment id A6. Fix circuit id B6. Install earth cable |  | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1609 | Ashik Kasim | 2023-09-21 11:25 | A6. Pending A6. Pending B6. Pending | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1610 | 6B29B64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar D Air Filter | 55.6190726,24.977695 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | Not Available | Not Available | Solenoid Valve -2 Solar Air Filter | GOYEN | RCA3-6V | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | D | T4 | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available B6. Earth cable not installed | A6. Fix equipment id A6. Fix circuit id B6. Install earth cable |  | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1610 | Ashik Kasim | 2023-09-21 11:28 | A6. Pending A6. Pending B6. Pending | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1611 | 1691A64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar D Air Filter | 55.6190057,24.9776498 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | Not Available | Not Available | Solenoid Valve -1 Solar Air Filter | GOYEN | RCA3-6V | Not Available | Instrumentation | Not Available | Not Available | NEC | Class 1 | D | T4 | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available B6. Earth cable not installed | A6. Fix equipment id A6. Fix circuit id B6. Install earth cable |  | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1611 | Ashik Kasim | 2023-09-21 11:30 | A6. Pending A6. Pending B6. Pending | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1612 | 552BB64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar D | 55.6190745,24.9774211 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | Not Available | 30-IC-125 | Gen Control Box - DC | Hoffman | Not Available | Not Available | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A9. Unauthorized modifications A9. Additional holes drilled A1. Ex data not available A10. Weather seal damaged A10. Non certified blanking elements installed A10. Wrong type locknuts installed | A6. Fix equipment id A9. Repair or replace equipment A9. Replace equipment A1. Replace equipment unless proven otherwise A10. Replace with suitable type glands A10. Replace with suitable type blanking elements A10. Replace with suitable type locknuts |  | 7 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1612 | Ashik Kasim | 2023-09-21 15:32 | A6. Pending A9. Pending A9. Pending A1. Pending A10. Pending A10. Pending A10. Pending | 7 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable
1613 | 0591A64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar D | 55.6191643,24.9779405 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | Not Available | 30-IC-108 | Gen Control Box - DC volt package JB | Hoffman | Not Available | Not Available | Electrical | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A9. Unauthorized modifications A9. Additional holes drilled A1. Ex data not available A10. Non certified blanking elements installed | A6. Fix equipment id A9. Repair or replace equipment A9. Replace equipment A1. Replace equipment unless proven otherwise A10. Replace with suitable type blanking elements |  | 5 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1613 | Ashik Kasim | 2023-09-21 15:36 | A6. Pending A9. Pending A9. Pending A1. Pending A10. Pending | 5 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable
1614 | 312CB64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar D | 55.6191697,24.9779251 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-JB-07 | 30-IC-3291 | Junction Box -Instrument | Weidmuller | NEXT 3030164 | UK-XA-GB-L-6132 | Electrical | 2 | Not Available | IEC | Ex e | IIC | T6 | IP66 | Not Available | KEMA | KEMA99ATEX7540X | Yes | Others | Periodic | d | Close | B6. Earth cable not installed | B6. Install earth cable |  | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1614 | Ashik Kasim | 2023-09-21 15:42 | B6. Pending | 1 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1615 | 302DB64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar D | 55.6191468,24.9779235 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-LG 07 | Not Available | Power Socket -240VAC | Course Hinds | CESD2213 | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 | D | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed A10. Multiple adaptors/reducers used | A6. Fix circuit id B6. Install earth cable A10. Replace with single adaptor/reducer |  | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1615 | Ashik Kasim | 2023-09-21 15:46 | A6. Pending B6. Pending A10. Pending | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1616 | 6B90A64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar D | 55.6191323,24.977921 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-LG 09 | Not Available | Power Socket -240VAC | Course Hinds | CESD2213 | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 | D | Not available | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed A10. Multiple adaptors/reducers used | A6. Fix circuit id B6. Install earth cable A10. Replace with single adaptor/reducer |  | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1616 | Ashik Kasim | 2023-09-21 15:50 | A6. Pending B6. Pending A10. Pending | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1617 | 792BB64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar D | 55.6191307,24.9779229 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-BD-10-SF10 | 30-C469 | LCS -Suppy Fan | Crouse Hinds | DSD922 | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close | B6. Earth cable not installed A10. Non certified blanking elements installed A10. Multiple adaptors/reducers used | B6. Install earth cable A10. Replace with suitable type blanking elements A10. Replace with single adaptor/reducer |  | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1617 | Ashik Kasim | 2023-09-21 15:58 | B6. Pending A10. Pending A10. Pending | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1618 | 4B2BB64C080104E0 |  | Margham | Area 25 | MEC-Compressor B | 55.6180757,24.9748725 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-GT-221B | 25-GT-221B | GAS DETECTOR TRANSMITTER | MSA | UltimaX5000 | 000100000128008B | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | Not Available | -40 +60 | SIRA | IECEX SIR17.0017X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1618 | Ashik Kasim | 2023-09-22 08:21 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1619 | 1592A64E080104E0 |  | Margham | Area 25 | MEC-Compressor B | 55.6180627,24.9748829 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-GT-221A | 25-GT-221A | GAS DETECTOR TRANSMITTER | MSA | UltimaX5000 | 0001000001280070 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | Not Available | -40 +60 | SIRA | IECEX SIR17.0017X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1619 | Ashik Kasim | 2023-09-22 08:28 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1620 | F029B64C080104E0 |  | Margham | Area 25 | MEC-Compressor B | 55.6180019,24.9746028 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-GT-321B | 25-GT-321B | GAS DETECTOR TRANSMITTER | MSA | UltimaX5000 | 0001000001280034 | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | Not Available | -40 +60 | SIRA | IECEX SIR17.0017X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1620 | Ashik Kasim | 2023-09-22 08:44 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1621 | 6491A64E080104E0 |  | Margham | Area 25 | MEC-Compressor B | 55.6179903,24.9746791 | Zone 2 | IIB | T3 | IP65 | EE-25-A1-609-01 | EE-25-A1-609-02 | 25-GT-321A | 25-GT-321A | GAS DETECTOR TRANSMITTER | MSA | UltimaX5000 | 000100000128009C | Instrumentation | 2 | Gb | IEC | Ex db | IIC | T5 | Not Available | -40 +60 | SIRA | IECEX SIR17.0017X | Yes | Others | Periodic | d | Close |  |  |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable |  | Data Sheet 1621 | Ashik Kasim | 2023-09-22 08:48 |  | 0 |  | Green | Not Applicable | Good to Use | Not Applicable | Not Applicable
1622 | EC8FA64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top | 55.61902,24.9774496 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-FT-0047 | Not Available | Flow Transmitter - Solar B | Rosemount | Not visible | Not Available | Instrumentation | Not Available | Not Available | NEC | Not Available | Not Available | Not available | Not Available | Not visible | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | A10. Non certified blanking elements installed(need to verify) B6. Earth cable not installed A1. Non conformant equipment A6. Circuit id not available | A10. Replace with suitable type blanking elements B6. Install earth cable A1. Replace equipment unless proven otherwise A6. Fix circuit id |  | 4 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1622 | Ashik Kasim | 2023-09-22 10:03 | A10. Pending B6. Pending A1. Pending A6. Pending | 4 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable
1623 | C72AB64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar B | 55.6189894,24.977466 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | Not Available | Not Available | Ex d Enclosure - Air Filter Control Solar B | Killark | Not Available | 1031 | Electrical | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | FM | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available B3. Trunking, ducts or pipes not sealed properly A10. Bolts missing A10. Wrong type bolts installed B6. Earth cable not installed A22. Damaged breathing and draining devices | A6. Fix equipment id A6. Fix circuit id B3. Apply sealing compound or device A10. Fix with manufacture recommended bolts A10. Replace with suitable type bolts B6. Install earth cable A22. Repair equipment by maintaining the IP |  | 7 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1623 | Ashik Kasim | 2023-09-22 10:30 | A6. Pending A6. Pending B3. Pending A10. Pending A10. Pending B6. Pending A22. Pending | 7 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1624 | 682BB64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top | 55.619033,24.9775063 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | Not Available | Not Available | LCS- Air filter -Solar B | Killark | FXCS-0S3C5 | Not Available | Electrical | Not Applicable | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | Not visible | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available A10. Multiple adaptors/reducers used B6. Earth cable not installed B3. Trunking, ducts or pipes not sealed properly | A6. Fix equipment id A6. Fix circuit id A10. Replace with single adaptor/reducer B6. Install earth cable B3. Apply sealing compound or device |  | 5 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1624 | Ashik Kasim | 2023-09-22 09:42 | A6. Pending A6. Pending A10. Pending B6. Pending B3. Pending | 5 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1625 | 5F2CB64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar B Air Filter | 55.6190232,24.9774626 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-GT-001B-F | Not Available | Solenoid Valve -1 Solar Air Filter B | Donaldson | Not Available | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 | D | T4 | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed | A6. Fix circuit id B6. Install earth cable |  | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1625 | Ashik Kasim | 2023-09-22 09:51 | A6. Pending B6. Pending | 2 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1626 | 932CB64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar B Air Filter | 55.619037,24.9775112 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | Not Available | Not Available | Solenoid Valve -2 Solar Air Filter B | Donaldson | Not Available | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 | D | T4 | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available B6. Earth cable not installed | A6. Fix equipment id A6. Fix circuit id B6. Install earth cable |  | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1626 | Ashik Kasim | 2023-09-22 09:55 | A6. Pending A6. Pending B6. Pending | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1627 | D32BB64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar B Air Filter | 55.6190464,24.9775044 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | Not Available | Not Available | Solenoid Valve -3 Solar Air Filter B | Donaldson | Not Available | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 | D | T4 | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available B6. Earth cable not installed | A6. Fix equipment id A6. Fix circuit id B6. Install earth cable |  | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1627 | Ashik Kasim | 2023-09-22 09:57 | A6. Pending A6. Pending B6. Pending | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1628 | BF2CB64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar B Air Filter | 55.61908,24.9774651 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | Not Available | Not Available | Solenoid Valve -4 Solar Air Filter B | Donaldson | Not Available | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 | D | T4 | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available B6. Earth cable not installed | A6. Fix equipment id A6. Fix circuit id B6. Install earth cable |  | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1628 | Ashik Kasim | 2023-09-22 09:59 | A6. Pending A6. Pending B6. Pending | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1629 | 9691A64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top Solar B | 55.6189615,24.9774636 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | Not Available | Not Available | Pressure Differential Transmitter | Rosemount | 3051S2CD1A73A1AKDL4M5 | 2213723 | Instrumentation | Not Available | Not Available | NEC | Class 1 Div 1 | BCD | Not available | Not Available | -50 +85 | FM | Not Available | Not Applicable | Others | Periodic | d | Close | A10. Non certified blanking elements installed(need to verify) B6. Earth cable not installed A6. Equipment id not available A6. Circuit id not available | A10. Replace with suitable type blanking elements B6. Install earth cable A6. Fix equipment id A6. Fix circuit id |  | 4 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1629 | Ashik Kasim | 2023-09-22 10:10 | A10. Pending B6. Pending A6. Pending A6. Pending | 4 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable
1630 | 5291A64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top | 55.6189501,24.9774172 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-GT-001B-EIBM | Not Available | LCS- Cooler Fan Lube Oil-Solar B | Killark | Not visible | Not Available | Electrical | Not Applicable | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed B3. Trunking, ducts or pipes not sealed properly | A6. Fix circuit id B6. Install earth cable B3. Apply sealing compound or device |  | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1630 | Ashik Kasim | 2023-09-22 10:12 | A6. Pending B6. Pending B3. Pending | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1631 | B790A64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top | 55.6190125,24.9774307 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-GT-001B-EIAM | Not Available | LCS- Cooler Fan Lube Oil-Solar B | Killark | Not visible | Not Available | Electrical | Not Applicable | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed B3. Trunking, ducts or pipes not sealed properly | A6. Fix circuit id B6. Install earth cable B3. Apply sealing compound or device |  | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1631 | Ashik Kasim | 2023-09-22 10:14 | A6. Pending B6. Pending B3. Pending | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1632 | F62BB64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top Solar B | 55.6189197,24.9773401 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | LB-10 | Not Available | Receptacle 240vac | FLP | simplex | Not Available | Electrical | Not Available | Not Available | NEC | Not Available | Not available | Not available | Not Available | Not Available | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | A1. Non conformant equipment A6. Circuit id not available A9. Unauthorized modifications(equipment painted) B6. Earth cable not installed B3. Trunking, ducts or pipes not sealed properly | A1. Replace equipment unless proven otherwise A6. Fix circuit id A9. Repair or replace equipment B6. Install earth cable B3. Apply sealing compound or device |  | 5 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1632 | Ashik Kasim | 2023-09-22 10:19 | A1. Pending A6. Pending A9. Pending B6. Pending B3. Pending | 5 |  | Red | 1 | Major Repair Required | Equipment Isolation | Not Applicable
1633 | 2992A64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top- Solar A | 55.618981,24.9773692 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | TPD-799 | Not Available | Pressure Differential Transmitter | Rosemount | 3051S2CD1A73A1AKDL4M5 | 2173457 | Instrumentation | Not Available | Not Available | NEC | Class 1 Div 1 | BCD | Not available | Not Available | -50 +85 | FM | Not Available | Not Applicable | Others | Periodic | d | Close | A10. Non certified blanking elements installed(need to verify) B6. Earth cable not installed A6. Equipment id not available A6. Circuit id not available A11. Loose cover | A10. Replace with suitable type blanking elements B6. Install earth cable A6. Fix equipment id A6. Fix circuit id A11. Tighten the cover |  | 5 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1633 | Ashik Kasim | 2023-09-22 10:23 | A10. Pending B6. Pending A6. Pending A6. Pending A11. Pending | 5 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable
1634 | C790A64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar A | 55.6188419,24.9774541 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | Not Available | Not Available | Ex d Enclosure - Air Filter Control Solar A | Killark | Not Available | 6827 | Electrical | Not Available | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | FM | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available B3. Trunking, ducts or pipes not sealed properly B6. Earth cable not installed | A6. Fix equipment id A6. Fix circuit id B3. Apply sealing compound or device B6. Install earth cable |  | 4 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1634 | Ashik Kasim | 2023-09-22 10:27 | A6. Pending A6. Pending B3. Pending B6. Pending | 4 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1635 | 832CB64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar A Air Filter | 55.6190204,24.9774084 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-GT-00IA-F | Not Available | Solenoid Valve -1 Solar Air Filter A | Donaldson | Not Available | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 | D | T4 | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed A10. Loose bolts | A6. Fix circuit id B6. Install earth cable A10. Tighten bolts |  | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1635 | Ashik Kasim | 2023-09-22 10:34 | A6. Pending B6. Pending A10. Pending | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1636 | 8391A64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar A Air Filter | 55.6190362,24.9774298 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | Not Available | Not Available | Solenoid Valve -2 Solar Air Filter A | Donaldson | Not Available | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 | D | T4 | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available B6. Earth cable not installed | A6. Fix equipment id A6. Fix circuit id B6. Install earth cable |  | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1636 | Ashik Kasim | 2023-09-22 10:37 | A6. Pending A6. Pending B6. Pending | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1637 | A52BB64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar A Air Filter | 55.6190271,24.9774054 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | Not Available | Not Available | Solenoid Valve -3 Solar Air Filter A | Donaldson | Not Available | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 | D | T4 | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available B6. Earth cable not installed | A6. Fix equipment id A6. Fix circuit id B6. Install earth cable |  | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1637 | Ashik Kasim | 2023-09-22 10:40 | A6. Pending A6. Pending B6. Pending | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1638 | 9C2BB64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Solar A Air Filter | 55.6189919,24.9773741 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | Not Available | Not Available | Solenoid Valve -4 Solar Air Filter A | Donaldson | Not Available | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 | D | T4 | Not Available | Not Available | CSA | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available B6. Earth cable not installed | A6. Fix equipment id A6. Fix circuit id B6. Install earth cable |  | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1638 | Ashik Kasim | 2023-09-22 10:42 | A6. Pending A6. Pending B6. Pending | 3 |  | Yellow | 4 | Minor Repair Required | Equipment Isolation | Not Applicable
1639 | EA29B64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top | 55.6189467,24.977353 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | Not Available | Not Available | LCS- Air filter -Solar A | Killark | FXCS-0S3C5 | Not Available | Electrical | Not Applicable | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | Not visible | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Equipment id not available A6. Circuit id not available A10. Multiple adaptors/reducers used B6. Earth cable not installed B3. Trunking, ducts or pipes not sealed properly | A6. Fix equipment id A6. Fix circuit id A10. Replace with single adaptor/reducer B6. Install earth cable B3. Apply sealing compound or device |  | 5 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1639 | Ashik Kasim | 2023-09-22 10:44 | A6. Pending A6. Pending A10. Pending B6. Pending B3. Pending | 5 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1640 | 5592A64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top | 55.6189716,24.9773518 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-FT-0046 | Not Available | Flow Transmitter - Solar A | Rosemount | Not visible | Not Available | Instrumentation | Not Available | Not Available | NEC | Not Available | Not Available | Not available | Not Available | Not visible | Not Available | Not Available | Not Applicable | Others | Periodic | d | Close | A10. Non certified blanking elements installed(need to verify) B6. Earth cable not installed A1. Non conformant equipment A6. Circuit id not available | A10. Replace with suitable type blanking elements B6. Install earth cable A1. Replace equipment unless proven otherwise A6. Fix circuit id |  | 4 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1640 | Ashik Kasim | 2023-09-22 10:48 | A10. Pending B6. Pending A1. Pending A6. Pending | 4 |  | Red | 2 | Major Repair Required | Equipment Isolation | Not Applicable
1641 | 7E2BB64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top | 55.6189729,24.9773448 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-GT-001A-EIAM | Not Available | LCS- Cooler Fan Lube Oil-Solar A | Killark | Not visible | Not Available | Electrical | Not Applicable | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed B3. Trunking, ducts or pipes not sealed properly A7. Damaged gasket(need to verify) | A6. Fix circuit id B6. Install earth cable B3. Apply sealing compound or device A7. Replace with manufacture recommended gasket |  | 4 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1641 | Ashik Kasim | 2023-09-22 10:51 | A6. Pending B6. Pending B3. Pending A7. Pending | 4 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1642 | B48FA64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top | 55.6189486,24.9773273 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-GT-001A-EIBM | Not Available | LCS- Cooler Fan Lube Oil-Solar A | Killark | Not visible | Not Available | Electrical | Not Applicable | Not Available | NEC | Class 1 | CD | Not available | Not Available | Not Available | UL | Not Available | Not Applicable | Others | Periodic | d | Close | A6. Circuit id not available B6. Earth cable not installed B3. Trunking, ducts or pipes not sealed properly | A6. Fix circuit id B6. Install earth cable B3. Apply sealing compound or device |  | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable |  | Data Sheet 1642 | Ashik Kasim | 2023-09-22 11:02 | A6. Pending B6. Pending B3. Pending | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Not Applicable
1643 | A32BB64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top | 55.6190018,24.9773449 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-LP-LA-04-03 | Not Available | LED Light Fixture | Appleton | MLLED4CBU | MY042106230159 | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T4 | IP66 | -40 +65 | CSA | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Circuit id not available B3. Trunking, ducts or pipes not sealed properly B6. Earth cable not installed | A6. Fix circuit id B3. Apply sealing compound or device B6. Install earth cable |  | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1643 | Ashik Kasim | 2023-09-22 11:12 | A6. Pending B3. Pending B6. Pending | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Scaffolding
1644 | D42AB64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top | 55.6189505,24.9772982 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-LP-AZ-08-02 | Not Available | LED Light Fixture | Appleton | MLLED4CBU | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T4 | IP66 | -40 +65 | CSA | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Circuit id not available B3. Trunking, ducts or pipes not sealed properly B6. Earth cable not installed | A6. Fix circuit id B3. Apply sealing compound or device B6. Install earth cable |  | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1644 | Ashik Kasim | 2023-09-22 11:21 | A6. Pending B3. Pending B6. Pending | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Scaffolding
1645 | 2F29B64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top | 55.6189296,24.9772871 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-LP-LA-06-02 | Not Available | LED Light Fixture | Appleton | MLLED4CBU | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T4 | IP66 | -40 +65 | CSA | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Circuit id not available B3. Trunking, ducts or pipes not sealed properly B6. Earth cable not installed | A6. Fix circuit id B3. Apply sealing compound or device B6. Install earth cable |  | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1645 | Ashik Kasim | 2023-09-22 11:24 | A6. Pending B3. Pending B6. Pending | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Scaffolding
1646 | B291A64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top | 55.6189294,24.9773389 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-LP-LA-06-03 | Not Available | LED Light Fixture | Appleton | MLLED4CBU | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T4 | IP66 | -40 +65 | CSA | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Circuit id not available B3. Trunking, ducts or pipes not sealed properly B6. Earth cable not installed | A6. Fix circuit id B3. Apply sealing compound or device B6. Install earth cable |  | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1646 | Ashik Kasim | 2023-09-22 11:26 | A6. Pending B3. Pending B6. Pending | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Scaffolding
1647 | 262DB64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top | 55.618948,24.9773961 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-LP-LA-06-07 | Not Available | LED Light Fixture | Appleton | MLLED4CBU | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T4 | IP66 | -40 +65 | CSA | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Circuit id not available B3. Trunking, ducts or pipes not sealed properly B6. Earth cable not installed | A6. Fix circuit id B3. Apply sealing compound or device B6. Install earth cable |  | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1647 | Ashik Kasim | 2023-09-22 11:28 | A6. Pending B3. Pending B6. Pending | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Scaffolding
1648 | 6429B64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top | 55.6189575,24.9774726 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-PAL-AZ-08-01 | Not Available | LED Light Fixture | Appleton | MLLED4CBU | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T4 | IP66 | -40 +65 | CSA | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Circuit id not available B3. Trunking, ducts or pipes not sealed properly B6. Earth cable not installed | A6. Fix circuit id B3. Apply sealing compound or device B6. Install earth cable |  | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1648 | Ashik Kasim | 2023-09-22 11:31 | A6. Pending B3. Pending B6. Pending | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Scaffolding
1649 | 392CB64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top | 55.6189604,24.977511 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-LP-LA-04-02 | Not Available | LED Light Fixture | Appleton | MLLED4CBU | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T4 | IP66 | -40 +65 | CSA | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Circuit id not available B3. Trunking, ducts or pipes not sealed properly B6. Earth cable not installed | A6. Fix circuit id B3. Apply sealing compound or device B6. Install earth cable |  | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1649 | Ashik Kasim | 2023-09-22 11:42 | A6. Pending B3. Pending B6. Pending | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Scaffolding
1650 | 4A8EA64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top | 55.6189283,24.9776024 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-LP-LA-04-01 | Not Available | LED Light Fixture | Appleton | MLLED4CBU | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T4 | IP66 | -40 +65 | CSA | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Circuit id not available B3. Trunking, ducts or pipes not sealed properly B6. Earth cable not installed | A6. Fix circuit id B3. Apply sealing compound or device B6. Install earth cable |  | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1650 | Ashik Kasim | 2023-09-22 11:45 | A6. Pending B3. Pending B6. Pending | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Scaffolding
1651 | 3C91A64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top | 55.618925,24.9776612 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-LP-LA-06-06 | Not Available | LED Light Fixture | Appleton | MLLED4CBU | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T4 | IP66 | -40 +65 | CSA | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Circuit id not available B3. Trunking, ducts or pipes not sealed properly B6. Earth cable not installed | A6. Fix circuit id B3. Apply sealing compound or device B6. Install earth cable |  | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1651 | Ashik Kasim | 2023-09-22 11:50 | A6. Pending B3. Pending B6. Pending | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Scaffolding
1652 | 5292A64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top | 55.6189751,24.9776191 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-LP-AZ-08-04 | Not Available | LED Light Fixture | Appleton | MLLED4CBU | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T4 | IP66 | -40 +65 | CSA | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Circuit id not available B3. Trunking, ducts or pipes not sealed properly B6. Earth cable not installed | A6. Fix circuit id B3. Apply sealing compound or device B6. Install earth cable |  | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1652 | Ashik Kasim | 2023-09-22 11:51 | A6. Pending B3. Pending B6. Pending | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Scaffolding
1653 | AA91A64E080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top | 55.6189549,24.9776093 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-LP-LA-06-05 | Not Available | LED Light Fixture | Appleton | MLLED4CBU | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T4 | IP66 | -40 +65 | CSA | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Circuit id not available B3. Trunking, ducts or pipes not sealed properly B6. Earth cable not installed | A6. Fix circuit id B3. Apply sealing compound or device B6. Install earth cable |  | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1653 | Ashik Kasim | 2023-09-22 11:52 | A6. Pending B3. Pending B6. Pending | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Scaffolding
1654 | 7B29B64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top | 55.6189584,24.9776172 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-LP-AZ-08-03 | Not Available | LED Light Fixture | Appleton | MLLED4CBU | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T4 | IP66 | -40 +65 | CSA | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Circuit id not available B3. Trunking, ducts or pipes not sealed properly B6. Earth cable not installed | A6. Fix circuit id B3. Apply sealing compound or device B6. Install earth cable |  | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1654 | Ashik Kasim | 2023-09-22 11:53 | A6. Pending B3. Pending B6. Pending | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Scaffolding
1655 | 7529B64C080104E0 |  | Margham | Area 30 | Solar Generator BLDG- Top | 55.6189518,24.9776195 | Zone 2 | IIB | T3 | IP54 | EE-30-A-0-660-01 |  | 30-LP-LA-06-04 | Not Available | LED Light Fixture | Appleton | MLLED4CBU | Not Available | Electrical | Not Available | Not Available | NEC | Class 1 Div 2 | ABCD | T4 | IP66 | -40 +65 | CSA | Not Available | Not Applicable | Lighting | Periodic | d | Close | A6. Circuit id not available B3. Trunking, ducts or pipes not sealed properly B6. Earth cable not installed | A6. Fix circuit id B3. Apply sealing compound or device B6. Install earth cable |  | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Scaffolding |  | Data Sheet 1655 | Ashik Kasim | 2023-09-22 12:00 | A6. Pending B3. Pending B6. Pending | 3 |  | Yellow | 3 | Minor Repair Required | Equipment Isolation | Scaffolding